G R A Y L I N X

Synex

Synex Copilot · Reports · Work Orders · Reliability · Intelligent Operations

Master Product & Architecture Document

Product → Copilot → Features → Flows → Cases → Architecture → Governance

Version 2.0  ·  Product-first edition

Prepared for Graylinx

# Contents

How to Read This Document	5

Executive Summary	7

PART ONE — The Product	10

1. What We Are Giving Users	11

2. The Product Story in One Flow	12

3. The Synex Copilot — The Kingpin of Graylinx	13

3.1 What the Copilot is — and what it is not	13

3.2 The fourteen operating modes	13

3.3 Anatomy of one Copilot turn	14

3.4 Context — how the Copilot understands “this”	14

3.5 Intent routing	15

3.6 The Copilot tool belt	16

3.7 The Control Plane interlock	18

3.8 The answer contract	18

3.9 Memory and state	19

3.10 Model routing across the four local models	19

3.11 Worked example — investigate a chiller fault	19

3.12 Worked example — act, then prove it worked	21

3.13 Reports and Work Orders are Copilot skills	22

3.14 What the Copilot must never do	22

3.15 How we will know the Copilot is good	22

4. User Flow — What Happens When Someone Uses AI	24

5. The Copilot in Practice — Levels and Conversations	25

5.1 Conversational feature levels	25

5.2 Copilot end-to-end workflow	25

5.3 Example conversations	25

5.4 Copilot conversations by role	25

6. Feature Catalogue at a Glance	27

7. Feature Domains in Detail	28

7.1 Feature map	28

7.2 Feature domains — what Graylinx can deliver	28

8. Reports	30

8.1 Report features	30

8.2 Report workflow — question to evidence	30

8.3 Report cases	30

8.4 Report scope, controls and governance	30

9. Work Orders	32

9.1 WO features	32

9.2 WO workflow cases	32

9.3 Work order non-negotiables	32

10. Equipment and Asset Intelligence	34

11. What Is ML, What Is Rules, What Is the LLM	35

12. Reliability and Fault Detection	37

12.1 Reliability case	37

12.2 RELIABILITY AI	37

13. Knowledge and Document Intelligence	38

14. Planning, People and Inventory	39

14.1 Planning example	39

14.2 PLANNING, INVENTORY AND ALERT AI	39

15. Alerts and Escalation	40

16. Verification and Learning	41

16.1 Learning workflow	41

17. Customer, Executive and Technician Experiences	42

18. Safety — Help, Never Bypass	43

19. Cases — How the Features Work Together	44

19.1 Complete Example — Fault → Fix → Proof → Report	45

20. End-to-End Business Cases	46

21. Role-Based Examples	47

22. What Is New in Graylinx — Product Positioning	48

23. Product Rules for Every New AI Feature	49

24. Delivery Priorities and Roadmap	50

24.1 FEATURE PRIORITY — WHAT WE SHOULD BUILD FIRST	50

25. Product North Star	51

PART TWO — Architecture & Engineering	52

26. Executive Product Definition	53

26.1 Priority hierarchy	53

26.2 High-level to low-level design	53

27. Personas and Role Architecture	54

27.1 Authorization model	54

28. Enterprise Architecture — High Level	55

28.1 High-level product flow	55

29. Agentic and Model Architecture	56

29.1 Agent families	56

29.2 Agent registry	56

30. The Equipment ML Layer — Inventory, Lifecycle and Trust	57

31. Low-Level Engineering Contracts	61

31.1 Tool contract	61

31.2 Policy decision contract	61

31.3 Evidence pack contract	61

32. The AI Control Plane	62

33. Security, Safety and Threat Model	63

33.1 Safety action matrix	63

33.2 Break-glass	63

34. Data, RAG and Report Governance	64

34.1 Data product contract	64

34.2 RAG rules	64

34.3 Report lineage	64

35. Priority Workflows	65

35.1 Report → Insight → Action	65

35.2 Fault → Fix → Proof	65

35.3 Technician workflow	65

35.4 Executive workflow	65

35.5 Unallowed workflow	65

35.6 Bad-data workflow	65

36. Feature → Agent → Control → Outcome Matrix	66

37. Validation, Testing and Production Acceptance	67

37.1 Release gates	67

38. Observability, Service Targets and Operations	68

38.1 Resilience	68

39. AI Governance, Change and Learning	69

39.1 Human override	69

39.2 Policy simulation	69

40. Global-Standard Alignment	70

40.1 Governance operating cycle	70

40.2 Non-negotiable global practices	70

41. Business Value and ROI	71

42. Implementation Blueprint	72

42.1 Service boundaries	72

42.2 Minimum state domains	72

42.3 Transaction rule	72

43. Gap Closure Checklist	73

44. Final Architecture Review	74

APPENDIX — Reference	75

Appendix A — Plain-English Feature Guide	76

# How to Read This Document

The product sections of this document are written in plain English. The architecture sections use the precise technical term, because engineers, auditors and security reviewers need the exact word. This table maps one to the other. Every term below means the same thing everywhere in the document.

| Term | Plain English meaning |
| --- | --- |
| Copilot | The single AI assistant users talk to. It is the front door to the whole platform. |
| Agent | A specialised worker inside the platform that handles one kind of job, such as reliability or planning. Users never address agents directly. |
| Tool | A single controlled action the AI is allowed to perform, such as “get health” or “create work order”. |
| Tool gateway | The layer that checks and executes every tool call, attaches credentials and writes the audit record. |
| Control Plane | The system that decides whether an action is allowed. The AI decides what it wants to do; the Control Plane decides whether it may. |
| Scope | The exact set of customers, sites, equipment and data one person is allowed to see or change. |
| Tenant | One customer account, kept completely separate from every other customer account. |
| Evidence | The real data behind an answer: readings, timestamps, model versions, records and documents. |
| Evidence pack | The bundle of evidence assembled for one answer, kept with the answer so it can be checked later. |
| Grounding | Checking that every statement the AI makes is supported by the evidence it retrieved. |
| Hallucination | An AI statement that sounds right but is not supported by any real data. Grounding exists to catch these. |
| Lineage | Where a number came from and how it was calculated, all the way back to the source record. |
| FDD | Fault Detection and Diagnosis — the existing Graylinx models and rules that find and classify equipment faults. |
| Model residual | The difference between what a sensor actually reads and what the normal-operation model predicted it should read. |
| Operating gate | A check that the equipment is in a valid state (running steady, above minimum load, valid flows) before any fault rule is allowed to fire. |
| Persistence | How long a pattern must hold before it counts as a fault rather than a passing disturbance. |
| NO_DIAGNOSIS | The honest answer the platform gives when the evidence is not good enough to name a cause. |
| RAG | Retrieval-augmented generation — the AI searches approved documents and answers from what it finds, with the sources shown. |
| SOP | Standard operating procedure — the approved way a task must be carried out. |
| Verification | Proving after the work that the problem is actually fixed, using post-work evidence rather than the work order status. |
| Criticality | How important a piece of equipment is to production, safety and cost. |
| Escalation | Sending an issue to the right person or team when a rule requires it. |
| Approval | A named human agreeing to an action before it happens. The AI can prepare an approval request but never grants one. |
| Idempotency | A safety property meaning a repeated request cannot create a duplicate — a retried work order is still one work order. |
| Degraded mode | A reduced but safe way of operating when part of the system is unavailable. The platform says when it is in this mode. |
| Audit trail | The permanent record of who asked, what was decided, what ran and what changed. |
| Break-glass | Temporary emergency access that is explicitly granted, fully recorded and expires automatically. |
| Prompt injection | An attack where text hidden in a document tries to give the AI instructions. Retrieved text is always treated as data, never as instructions. |
| Release gate | A test the platform must pass before a new version reaches customers. |
| Digital twin | The platform’s model of a real asset, including its normal behaviour and its history. |
| Work order (WO) | The record of a maintenance job: what must be done, by whom, when, and what was found. |
| Normal-operation model | A model trained on how the equipment behaves when it is healthy. It predicts what a reading should be, so we can measure how far reality has moved away from it. |
| Operating envelope | The range of loads and temperatures a model was trained on. Outside that range its prediction is not trustworthy. |
| Model drift | A model slowly becoming wrong because the equipment, the controls or the duty have changed since it was trained. |
| Model registry | The controlled list of every model in production — its version, inputs, owner, error band and status. |
| Quarantine | What happens to a model that fails its health check: its output stops being used for diagnosis until it is fixed or retrained. |
| Re-baseline | Retraining a model on a new definition of normal, after the equipment or its controls have legitimately changed. |
| Efficiency proxy | A calculated indicator of how well the chiller is moving heat, derived from the two water-side temperature differences and their flows. |
| SLA | The agreed service level — for example how quickly critical work must be started or completed. |

# Executive Summary

Graylinx is an AI-native maintenance and reliability platform for the whole company. Its primary customer experiences are Reports, Work Orders and Synex Copilot. Existing ML and FDD provide equipment intelligence; the AI that can plan and use tools layer turns that intelligence into governed decisions and actions; the Control Plane makes those actions secure, scoped, evidence-based and grounded, approved where required, auditable and verifiable.

The complete loop:

SENSE → UNDERSTAND → DIAGNOSE → EXPLAIN → DECIDE → CREATE/EXECUTE WORK → VERIFY → LEARN → REPORT VALUE

High-level architecture defines the platform. Workflows define how users and systems operate it. Low-level contracts define implementation. Validation, service targets, audit and governance prove it works in production.

The target is not maximum autonomy. The target is maximum useful feature under explicit, testable and auditable control.

| Token | HEX | Use | Guidance |
| --- | --- | --- | --- |
| Primary — Graylinx Blue | #2563EB | Primary buttons, links, active navigation, selected states | Use for interactive/product identity, not for alarms. |
| Primary Dark | #1D4ED8 | Hover/pressed states, strong headings where needed | Maintain contrast. |
| Deep Navy | #0F172A | Top-level text, headers, high-emphasis UI | Main enterprise/technical anchor. |
| Slate | #334155 | Secondary text, labels, metadata | Readable supporting information. |
| Muted Slate | #64748B | Helper text, timestamps, secondary metadata | Do not use for critical content. |
| Canvas | #F8FAFC | Application background | Default light workspace. |
| Surface | #FFFFFF | Cards, panels, tables, dialogs | Primary content surface. |
| Border | #E2E8F0 | Dividers, card borders, table lines | Keep subtle. |
| Success | #16A34A | Healthy, verified, completed, approved | Pair with icon/text. |
| Warning | #D97706 | Attention, degraded mode, pending, approaching SLA | Not for hard failure. |
| Critical / Error | #DC2626 | Fault, failed, blocked, safety-critical | Use sparingly and consistently. |
| Info | #0891B2 | Informational states, guidance, neutral system notices | Use for contextual information. |
| AI Accent | #7C3AED | AI/Copilot identity, generated insight markers | Use only to distinguish AI—not as a general status color. |

| Semantic state | Color token | Example | Always pair with |
| --- | --- | --- | --- |
| Healthy / Verified | Success | #16A34A | ✓ icon + text |
| Attention / Pending | Warning | #D97706 | ⚠ icon + text |
| Fault / Failed | Critical | #DC2626 | ✕ icon + text |
| Information | Info | #0891B2 | i icon + text |
| created by AI | AI Accent | #7C3AED | AI badge/icon + label |
| Neutral / Unknown | Muted Slate | #64748B | Status text |

| Component | Recommended behavior | Example |
| --- | --- | --- |
| Global navigation | Role-aware; show core pillars first | Reports / Work Orders / Copilot / Assets |
| Synex Copilot | Persistent but non-intrusive entry point | Ask, explain, investigate, recommend, act |
| KPI cards | One metric + status + trend + open more detail | Availability 98.4% ↑ |
| Asset health card | Health + risk + evidence + next action | Chiller-03 / High risk / Why? |
| WO card | Priority + SLA + assignee + state + verification | Critical / Assigned / Verify |
| Evidence panel | Source + timestamp + model/FDD + confidence | Why AI says this |
| Approval dialog | Exact action + impact + evidence + approver | Approve WO |
| Safety gate | Prominent blocking state when required | Permit required |
| Report builder | Role/scope-aware filters + saved views | Plant → Asset → Period |
| Audit timeline | Human-readable chronological actions | Who / what / when / why |

| Level | Recommendation | Use |
| --- | --- | --- |
| Display / Page title | 28–32 px, semibold/bold | Major page titles |
| Section heading | 20–24 px, semibold | Dashboard/report sections |
| Card heading | 16–18 px, semibold | Modules and cards |
| Body | 14–16 px | Normal application text |
| Dense table | 12–14 px | Operational data |
| Metadata | 11–12 px | Timestamp/source/secondary data |

| Persona family | Primary UI emphasis | Copilot emphasis |
| --- | --- | --- |
| Executive | KPIs, risk, cost, availability, ROI | Explain enterprise performance; drill down |
| Plant / Operations | Plant health, production impact, alerts | What needs attention now? |
| Maintenance | Backlog, SLA, PM, WOs, people, parts | Prioritize, plan, draft and manage WOs |
| Technician | My Work, safety, SOP, findings, parts | Guide the job and verify repair |
| Reliability | FDD, bad actors, trends, evidence | Diagnose, compare, investigate |
| AI/ML / Data | Model/FDD/RAG quality and evidence | Evaluate and troubleshoot AI |
| EHS / Compliance | Safety gates, approvals, audit | Explain rule; never bypass safety |
| Admin / IT | Users, roles, integrations, health | Diagnose platform/configuration issues |
| Customer | Site performance, WOs, reports | Explain customer assets and service outcomes |

| Primary #2563EB | Navy #0F172A | Canvas #F8FAFC | Success #16A34A | Warning #D97706 | Critical #DC2626 | AI #7C3AED |
| --- | --- | --- | --- | --- | --- | --- |

# PART ONE

The Product

What every person in the organization can actually do with the new Graylinx AI platform — the Copilot, the features it reaches, the flows and the real cases.

# 1. What We Are Giving Users

The first thing the document should explain is what people can actually do with the new Graylinx AI platform. The architecture comes after that. The main customer experience is built around three core areas:

| Priority | Core feature | Simple promise |
| --- | --- | --- |
| P0 | Reports | Ask questions, understand what is happening, investigate why, and create useful reports. |
| P0 | Work Orders | Create, plan, execute, track and verify maintenance work with AI assistance. |
| P0 | Synex Copilot | One assistant that can understand the user, find the right information, explain it and help take approved actions. |

# 2. The Product Story in One Flow

Instead of making users move between many screens, Graylinx connects information and actions into one simple journey:

ASK → UNDERSTAND → FIND DATA → EXPLAIN → RECOMMEND → CREATE/ACT → VERIFY → REPORT → LEARN

Example: A manager asks, “What equipment needs attention today?” Graylinx finds the important equipment, explains why, shows the supporting data, offers the next action, can prepare a work order, and later checks whether the repair worked.

# 3. The Synex Copilot — The Kingpin of Graylinx

Reports and Work Orders are what the business needs. The Copilot is how people reach them. It is the front door to the whole Graylinx platform: one place where any person — executive, engineer, planner, technician or customer — can ask a question in their own words and get an answer that is scoped to them, backed by real data, and connected to the action that follows.

This section defines the Copilot completely: what it is, how one request travels through it, what it is allowed to touch, what it must say when it does not know, and how we will judge whether it is good. Everything that follows in this document — Reports, Work Orders, Asset intelligence, Reliability, Knowledge, Planning, Inventory, Alerts — is a capability the Copilot can reach.

PRODUCT PRINCIPLE The Copilot is not a feature of the platform. The Copilot is how the platform is used. Every other capability in this document is a skill the Copilot can call, through the Control Plane, with evidence and an audit trail.

## 3.1 What the Copilot is — and what it is not

| The Copilot IS | The Copilot IS NOT |
| --- | --- |
| The single entry point to Reports, Work Orders, Assets, Reliability, Knowledge, Planning, Inventory and Alerts. | A chat box added beside the existing screens that answers general questions. |
| A reasoning and explanation layer on top of the ML and FDD that Graylinx already has. | A replacement for the existing ML and FDD models. |
| An actor that can prepare and execute approved actions through typed tools. | A system that acts on its own authority or holds its own permissions. |
| Honest: it says NO_DIAGNOSIS when the evidence is not good enough. | A system that always produces a confident answer. |
| Traceable: every material answer carries its sources, timestamps and model versions. | A black box whose answers cannot be checked afterwards. |
| Scope-aware: it only ever sees what the person in front of it is allowed to see. | A shared brain that can quietly read across customers or sites. |
| Continuous: it follows a job from question to work order to verified result. | A one-shot question-and-answer tool that forgets the task. |

## 3.2 The fourteen operating modes

A user never chooses a mode. The Copilot works out what kind of request it is receiving and behaves accordingly. Each mode has a different control level, because reading data and changing data are not the same act.

| Mode | The user says | What the Copilot does | Writes? | Control level |
| --- | --- | --- | --- | --- |
| ASK | “What is the health of Chiller-03?” | Retrieves and states a fact with its source and timestamp. | No | Scope + permission |
| EXPLAIN | “Why is this unhealthy?” | Builds an evidence pack and gives the likely cause in plain English. | No | Evidence + grounding |
| INVESTIGATE | “What is really going on here?” | Runs a multi-step enquiry across FDD, trends, history and knowledge. | No | Evidence + gates |
| COMPARE | “Chiller-03 versus Chiller-04 this month.” | Aligns two scopes or periods on the same definitions and shows the difference. | No | Scope + metric definitions |
| SEARCH | “What does the manual say about approach temperature?” | Retrieves from SOPs, manuals, WO history and verified cases with sources. | No | Tenant + source scope |
| RECOMMEND | “What should we do about it?” | Proposes ranked next actions with the reason and the confidence for each. | No | Evidence + uncertainty |
| REPORT | “Give me this week’s reliability summary.” | Generates a role-appropriate report with KPI lineage. | Artifact | Scope + lineage |
| DRAFT | “Create a work order for this.” | Prepares a complete, validated WO draft and shows it before anything is saved. | No | Permission + validation |
| APPROVE | “Approve this critical work order.” | Presents the request to the human who holds the authority. It never approves itself. | No | Named human only |
| EXECUTE | “Yes, create it.” | Calls the write tool through the gateway with an idempotency key. | Yes | Policy + tool gateway |
| VERIFY | “Did the repair work?” | Compares post-work evidence against the fault signature and returns PASS / FAIL / UNKNOWN. | Result only | Evidence required |
| ESCALATE | “This is not safe.” | Routes to EHS, reliability or the supervisor per the escalation rule. | Yes | Policy + routing |
| MONITOR | “Tell me if this gets worse.” | Registers a watch on a condition and notifies when the rule fires. | Config | Owner + quota |
| SUMMARIZE | “Brief me on this week.” | Condenses many records into a short briefing with drill-down links. | No | Scope |

## 3.3 Anatomy of one Copilot turn

Every single request — from “what is the temperature” to “close this critical work order” — travels through the same fourteen stages. Stages are never skipped. If a stage cannot complete, the Copilot degrades to a weaker answer state (3.8); it does not proceed as if the stage had passed.

| # | Stage | What happens | Owned by | Budget |
| --- | --- | --- | --- | --- |
| 1 | Capture | Message, current screen, selected object and active filter are captured. | Copilot API | 50 ms |
| 2 | Identify | User, role, tenant and approval authority are resolved from the session. | Identity service | 50 ms |
| 3 | Scope | The allowed customer, site, system, asset and data scope is computed. | Control Plane | 100 ms |
| 4 | Resolve context | “this”, “it”, “the same one” are bound to real object IDs. | Router (phi4) | 300 ms |
| 5 | Classify intent | Mode and target skill are chosen; ambiguous requests trigger one question. | Router (phi4) | 300 ms |
| 6 | Pre-authorize | Is this class of request allowed for this person at all? | Control Plane | 100 ms |
| 7 | Plan | Decide which tools to call, in what order, and what evidence is needed. | Brain (gemma4) | 1–3 s |
| 8 | Retrieve | Read-only tools and retrieval run in parallel; results are typed. | Executor (devstral) | 0.5–3 s |
| 9 | Gate data quality | Freshness, operating state, sensor validity and persistence are checked. | Data-quality service | 200 ms |
| 10 | Reason | Evidence pack is assembled and the answer is formed. | Brain (gemma4) | 2–6 s |
| 11 | Ground and audit | Every claim is checked against the evidence pack; unsupported claims are cut. | Auditor (phi4) | 0.5–2 s |
| 12 | Decide action | For any write: ALLOW / ALLOW-WITH-APPROVAL / READ-ONLY / ESCALATE / DENY. | Control Plane | 200 ms |
| 13 | Execute | Write tool is called with a schema-valid payload and an idempotency key. | Tool gateway | 0.2–2 s |
| 14 | Respond and record | Answer, evidence and the full decision trail are returned and stored. | Copilot API + Audit | 200 ms |

Service targets: a read-only answer should complete within 8 seconds at p95, and a first token should appear within 2 seconds. An action turn — one that writes — should complete within 12 seconds at p95, excluding the time a human takes to approve.

SEPARATION RULE Stages 3, 6, 11 and 12 are outside the language models. The model may decide what it wants to do; it can never decide whether it is allowed to do it.

## 3.4 Context — how the Copilot understands “this”

The single biggest difference between a chatbot and a copilot is context. If a user is already looking at Customer → Plant A → Chiller System → Chiller-03 and asks “why is this bad?”, the Copilot must answer about Chiller-03 without being told.

| Context slot | Where it comes from | Example | If missing |
| --- | --- | --- | --- |
| WHO | Session identity | Ravi K., Reliability Engineer | Refuse — no anonymous turns |
| AUTHORITY | Role and approval matrix | May draft WOs; may not close critical WOs | Treat as read-only |
| TENANT | Account binding | Customer: Southern Mills Pvt Ltd | Refuse — never guess a tenant |
| SITE / PLANT | Screen or last explicit mention | Plant A, Madurai | Ask one question |
| SYSTEM | Asset hierarchy | Chilled water system | Infer from equipment |
| EQUIPMENT | Selected object | Chiller-03 | Ask one question |
| COMPONENT | Drill-down or fault subject | Condenser bundle | Optional |
| SCREEN | Client context payload | Asset health dashboard | Fall back to conversation |
| ACTIVE FILTER | Client context payload | Last 30 days, weekdays only | Use platform default and say so |
| ACTIVE OBJECT | Client context payload | Fault F-8842 / WO-2291 / Report R-114 | Fall back to conversation |
| CONVERSATION | Thread state | Two turns ago the user asked about Chiller-03 | Ask one question |
| TIME WINDOW | Request or default | This month; current shift | Use platform default and say so |
| PERMISSIONS | Control Plane decision | Read Plant A; no access to Plant C | Refuse the out-of-scope part |

### Reference resolution rules

Explicit beats implicit — An object the user names explicitly always wins over the object on screen.

Most recent wins — the most recent explicitly mentioned object of the right type is used.

Ambiguity is a question, not a guess — if two objects of the same type are equally plausible, ask one short question. Do not guess.

Scope is a hard wall — a reference is never resolved to an object outside the user’s scope. If the referenced object exists but is out of scope, the Copilot says so plainly rather than pretending it does not exist — unless the existence itself is confidential, in which case it reports no access.

Resolution is visible — when the Copilot resolves a reference, the resolved object is shown in the answer header, so the user can see what it understood.

## 3.5 Intent routing

The router turns a sentence into a mode plus a skill. This is a small, fast, cheap decision made by phi4, and it is measured: routing accuracy is a release gate (3.15). Low-confidence routing does not guess; it asks.

| Intent | Example utterance | Primary skill | Typical tools | Writes? |
| --- | --- | --- | --- | --- |
| asset_status | “How is Chiller-03 doing?” | Asset intelligence | get_asset, get_health | No |
| fault_explain | “Why did FDD raise this?” | Reliability | get_faults, explain_fault, get_residuals | No |
| root_cause | “What is actually causing the high power?” | Reliability | get_residuals, get_trends, find_similar_cases | No |
| trend_compare | “Is this worse than last month?” | Asset / Reports | get_trends, compare_assets | No |
| report_request | “Weekly maintenance summary for Plant A.” | Reports | create_report, get_report | Artifact |
| report_explain | “Why did availability drop?” | Reports | get_report, get_faults, get_wo | No |
| knowledge_lookup | “What is the inspection procedure?” | Knowledge | search_sop, search_manual | No |
| history_lookup | “How was this fixed last time?” | Knowledge | search_history, search_verified_cases | No |
| wo_create | “Raise a work order for this.” | Work orders | create_wo (after draft) | Yes |
| wo_manage | “Assign it to the day shift.” | Work orders | assign_wo, schedule_wo, update_wo | Yes |
| wo_close | “Close WO-2291.” | Work orders + Verification | verify_fault, close_wo | Yes |
| verify_outcome | “Did the repair work?” | Verification | get_residuals, get_wo, verify_fault | Result |
| planning | “What can we schedule tomorrow?” | Planning | find_window, find_technicians, check_availability | No |
| parts | “Do we have the gasket set?” | Inventory | check_part, check_delivery | No |
| alert_triage | “Why did I get 40 alerts?” | Alerts | get_faults, group and rank | No |
| safety_check | “Can I isolate this now?” | Safety | search_sop, policy check | No |
| admin_query | “Why can’t this user see the report?” | Platform | audit, permissions read | No |
| out_of_scope | “Write my performance review.” | — | None | No |

## 3.6 The Copilot tool belt

The Copilot does not reach the database, the CMMS or the historian directly. It reaches typed tools, and every tool call passes through the Tool Gateway, which validates the schema, applies scope, attaches short-lived credentials and writes the audit record. The columns below are the contract each tool must publish.

Class R = read only. Class W = writes to a system of record. Class A = produces an artifact (a report file, an export) but does not change operational state. Class C = changes configuration.

### Report tools

| Tool | What it does | Class | Risk | Approval | Idempotent |
| --- | --- | --- | --- | --- | --- |
| get_report | Returns an existing report within the user’s scope. | R | Low | None | n/a |
| create_report | Builds a report from a natural-language or structured spec. | A | Low | None | By spec hash |
| compare_reports | Aligns two reports on identical metric definitions. | R | Low | None | n/a |
| export_report | Exports to file or sends outside the platform. | A | Medium | Role-based | By export ID |
| schedule_report | Creates or edits a recurring delivery. | C | Medium | Owner | By schedule key |

### Asset tools

| Tool | What it does | Class | Risk | Approval | Idempotent |
| --- | --- | --- | --- | --- | --- |
| get_asset | Identity, make and model, criticality, ownership, hierarchy position. | R | Low | None | n/a |
| get_health | Current health score, status and contributing factors. | R | Low | None | n/a |
| get_history | Events, faults, work orders and readings for a period. | R | Low | None | n/a |
| get_dependencies | Upstream and downstream assets and served load. | R | Low | None | n/a |
| compare_assets | Side-by-side comparison of like assets on like conditions. | R | Low | None | n/a |

### FDD and ML tools

| Tool | What it does | Class | Risk | Approval | Idempotent |
| --- | --- | --- | --- | --- | --- |
| get_faults | Open and historical fault records with class, state and confidence. | R | Low | None | n/a |
| explain_fault | Returns the rule path and signals that produced a fault class. | R | Low | None | n/a |
| get_residuals | Model residuals per signal with the operating gates that applied. | R | Low | None | n/a |
| get_trends | Trend, volatility and rate of change over a window. | R | Low | None | n/a |
| find_similar_cases | Verified historical cases with a similar fault signature. | R | Low | None | n/a |
| verify_fault | Records a post-work verification outcome against the fault. | W | Medium | Supervisor if critical | By WO + fault |

### Work order tools

| Tool | What it does | Class | Risk | Approval | Idempotent |
| --- | --- | --- | --- | --- | --- |
| create_wo | Creates a work order from a validated draft. | W | Medium | Per policy and criticality | Client key |
| get_wo | Returns a work order and its full history. | R | Low | None | n/a |
| update_wo | Edits permitted fields on an open work order. | W | Medium | Owner or supervisor | By version |
| assign_wo | Assigns to a technician or crew. | W | Medium | Planner or supervisor | By assignment |
| prioritize_wo | Sets or changes priority using risk, criticality and SLA. | W | Medium | Supervisor if raised to P1 | By version |
| schedule_wo | Places the work in a maintenance window. | W | Medium | Planner | By window |
| add_finding | Records technician findings, readings and photographs. | W | Low | None | By finding ID |
| close_wo | Closes a work order. | W | High | Supervisor for critical; verification PASS required | By WO state |
| reopen_wo | Reopens after a failed or unproven repair. | W | Medium | Supervisor | By WO state |

### Knowledge tools

| Tool | What it does | Class | Risk | Approval | Idempotent |
| --- | --- | --- | --- | --- | --- |
| search_sop | Retrieves approved standard operating procedures. | R | Low | None | n/a |
| search_manual | Retrieves manufacturer documentation for the asset model. | R | Low | None | n/a |
| search_history | Retrieves past work orders and findings. | R | Low | None | n/a |
| search_verified_cases | Retrieves cases where the fix was proven to work. | R | Low | None | n/a |

### Planning and inventory tools

| Tool | What it does | Class | Risk | Approval | Idempotent |
| --- | --- | --- | --- | --- | --- |
| find_technicians | Finds people with the required skills and certifications. | R | Low | None | n/a |
| check_availability | Returns availability across shifts and leave. | R | Low | None | n/a |
| find_window | Finds a production-compatible maintenance window. | R | Low | None | n/a |
| plan_work | Produces a proposed plan for human confirmation. | W | Medium | Planner | By plan ID |
| check_part | Checks stock, location and alternates. | R | Low | None | n/a |
| reserve_part | Reserves stock against a work order. | W | Medium | Value threshold | By reservation |
| check_delivery | Returns expected delivery and its effect on the schedule. | R | Low | None | n/a |

### Platform tools

| Tool | What it does | Class | Risk | Approval | Idempotent |
| --- | --- | --- | --- | --- | --- |
| notifications | Sends a scoped notification to a person or group. | W | Low | Rate-limited | By message key |
| approvals | Raises an approval request and tracks its state. | W | High | Never self-approved | By request |
| audit | Reads the decision and action trail. | R | Restricted | Auditor role | n/a |
| escalation | Routes an issue per the escalation matrix. | W | Medium | Policy | By incident |

### Tool rules that are not negotiable

Typed — Every tool publishes a versioned input and output schema, and the gateway rejects anything that does not validate.

No free SQL on writes — Natural language to SQL is allowed only against curated read-only views. There is no generated SQL on any write path.

Idempotent writes — Every write carries an idempotency key, so a retry after a timeout can never create a duplicate work order.

No credentials in the model — The model never sees a credential. The gateway brokers short-lived, scoped credentials per call.

Results are data, not instructions — Text returned by a tool or a document is data. If it contains something that looks like an instruction, it is ignored and flagged.

Least privilege — A tool the Copilot has not been granted does not appear in its tool list at all, so it cannot be tricked into calling it.

Read-only on hardware — No tool issues a direct control command to plant equipment. Equipment control remains outside the agentic layer.

## 3.7 The Control Plane interlock

The Copilot decides what it wants to do. The Control Plane decides whether it may. These are separate systems, and the Copilot cannot call a write tool except through a Control Plane decision.

REQUEST → IDENTITY → SCOPE → INTENT → RISK CLASS → SAFETY GATE → APPROVAL RULE → DECISION → TOOL GATEWAY → EXECUTION → AUDIT

| Decision | When it is returned | What the user sees | What is recorded |
| --- | --- | --- | --- |
| ALLOW | In scope, low risk, no approval rule applies. | The action happens and the result is shown. | Actor, action, inputs, result, policy version |
| ALLOW-WITH-APPROVAL | Permitted, but the action class or value needs a named approver. | A prepared request, the approver’s name, and its status. | Request, approver, decision, timestamps |
| READ-ONLY | The person may see it but not change it. | The full answer, with the action offered as a request to someone else. | Attempted action and downgrade reason |
| ESCALATE | Safety-critical, or a rule requires another function to judge. | Who it went to and why. | Escalation route and rule version |
| DENY | Out of scope, forbidden action, or a failed safety gate. | A plain reason and what to do instead. | Denial reason and rule version |

DENIAL IS AN ANSWER A denial is a product feature, not an error. The Copilot explains what was blocked, which rule blocked it, and what the person can do next — request approval, ask a named colleague, or correct the data.

## 3.8 The answer contract

Every Copilot turn ends in exactly one of six states. The state is explicit in the response, not implied by tone. This is what stops the Copilot from sounding confident when it is not.

| State | When it is used | What the user gets |
| --- | --- | --- |
| ANSWERED | Evidence is sufficient and grounded. | The answer, the confidence word, the evidence, and the offered next action. |
| PARTIAL | Part of the question is answerable; part is out of scope or unavailable. | What is known, plainly marked, plus exactly what is missing and why. |
| NO_DIAGNOSIS | Operating gates failed, data is stale or invalid, or signals conflict. | A statement that no diagnosis can be made, which check failed, and a data-quality action. |
| NEEDS_APPROVAL | The action is permitted but requires a named human. | The prepared action, the approver, and the request status. |
| BLOCKED | Scope, permission or safety rule prevents the request. | The reason, the rule, and the correct route. |
| FAILED | A tool or dependency failed after retries. | What failed, what was and was not done, and the safe next step. |

### Confidence language

The Copilot uses four words and only four, so that the same word always means the same thing across the platform:

| Word | Meaning | Requirement |
| --- | --- | --- |
| Confirmed | Directly measured or recorded. | A source record with a timestamp. |
| Likely | One fault class fits the evidence and the alternatives do not. | All gates passed; competing classes ruled out. |
| Possible | Evidence fits more than one explanation. | Alternatives must be listed, not hidden. |
| Not enough evidence | Gates failed or required signals are missing. | Must state which signal or gate is the problem. |

### When the Copilot must refuse to diagnose

The equipment is not in a valid operating state — starting, stopping, below minimum load, or in a setpoint change.

A required model input is missing or invalid, so the model’s residual cannot be trusted.

The pattern has not persisted long enough to be a fault rather than a transient.

Two independent signals contradict each other and no rule separates them.

The most recent data is older than the freshness threshold for that decision.

In all five cases the correct output is NO_DIAGNOSIS plus a data-quality or instrumentation action — never a softened guess.

## 3.9 Memory and state

| Memory | What it holds | Lifetime | Notes |
| --- | --- | --- | --- |
| Turn context | Screen, selected object, filter, resolved references. | One turn | Rebuilt every turn from the client payload. |
| Conversation thread | Previous questions, resolved objects, offered actions. | Session, then archived | Scope re-checked every turn — it is never inherited. |
| Task state | A multi-step job: investigate → draft → approve → execute → verify. | Until closed or expired | Durable, resumable, survives a dropped session. |
| Watches | Conditions the user asked to be told about. | Until cancelled | Owned by a person, counted against a quota. |
| User preferences | Units, default period, report format, language. | Persistent | Preferences never widen scope. |
| Verified-case memory | Fault signature → fix → proven outcome. | Persistent | Tenant-isolated. Feeds find_similar_cases. |

### Never remembered

Credentials, tokens or connection strings of any kind.

Any data belonging to another tenant, in any form, including aggregates and counts.

A previous approval, as authority for a later action. Every action is authorized on its own.

A previously granted scope. Scope is recomputed on every turn from the live permission set.

## 3.10 Model routing across the four local models

Graylinx runs four models locally. They are not interchangeable, and the Copilot routes each stage of a turn to the model suited to it. Nothing in this document requires a fifth model.

| Model | Size | Environment | Used at stages | Why this model |
| --- | --- | --- | --- | --- |
| gemma4:26b-a4b-it-qat | ~16 GB | OLLAMA_MODEL_BRAIN | 7 Plan, 10 Reason | Strongest reasoning; writes the explanation the user reads. |
| devstral:latest | ~14 GB | OLLAMA_MODEL_TOOL | 8 Retrieve | Reliable structured tool calling, ReAct loop and read-only NL→SQL. |
| phi4 | 9.1 GB | OLLAMA_MODEL_TEXT / _AUDITOR / _RAG / _DEFAULT | 4 Resolve, 5 Classify, 11 Ground, narration | Fast and cheap for short decisions; independent of the brain for auditing. |
| nomic-embed-text | 274 MB | — | Retrieval indexing and query | 768-dimension local embeddings; content never leaves the site. |

### Routing rules

Separation of duties — The brain reasons and explains but never calls a tool directly; the executor calls tools but never writes the final answer to the user.

Auditor independence — The model that grounds and audits an answer is not the model that produced it. Shared weights produce correlated blind spots, so the auditor must be phi4 whenever the brain wrote the answer.

Cheap decisions stay cheap — Routing and reference resolution use the small model. If routing confidence is low, the Copilot asks the user rather than escalating to a larger model and guessing.

Embeddings stay local — Embeddings are always computed locally and never sent to a remote service.

Degraded mode is declared — If the brain is unavailable, the Copilot serves ASK, SEARCH and REPORT in a degraded mode and refuses EXPLAIN, INVESTIGATE and RECOMMEND, saying so. It does not silently substitute a weaker model for reasoning.

## 3.11 Worked example — investigate a chiller fault

This example uses the real water-cooled chiller FDD engine: six residuals from normal-operation models, with operating gates applied before any rule is allowed to fire. A residual is the difference between what a signal actually reads and what the normal-operation model predicted it should read.

Context: Ravi K., Reliability Engineer, is on the Chiller-03 asset page for Plant A. He types: “Why is this unhealthy?”

### Stage 1–6 — who, what and whether

Identity resolves to Ravi K., Reliability Engineer, tenant Southern Mills, scope Plant A and Plant B. “this” resolves from the screen to Chiller-03, and the resolved object is shown in the answer header. Intent classifies as fault_explain, mode EXPLAIN. Pre-authorization returns ALLOW — this is a read.

### Stage 8–9 — evidence and gates

The executor calls get_faults, get_residuals, get_trends, get_history and find_similar_cases in parallel. Before any rule runs, the operating gates are checked.

| Gate | Requirement | Reading | Result |
| --- | --- | --- | --- |
| Running steady | No start or stop transient | Steady 4 h 20 min | PASS |
| Load above minimum | Above the model’s valid load floor | 68% load | PASS |
| Flows valid | Evaporator and condenser flow signals healthy | Both valid | PASS |
| No setpoint change | No leaving-water setpoint move in the window | None | PASS |
| Persistence | Pattern held 20–30 min or more | Held 42 min | PASS |

| Signal | Residual | Reading | What it means |
| --- | --- | --- | --- |
| Chiller power | rPwr | High | The chiller is using more power than the model expects for these conditions. |
| Discharge pressure | rDP | High | Head pressure is higher than expected. |
| Condenser water leaving | rCWL | High | Heat is not being rejected into the condenser water properly. |
| Suction pressure | rSP | Normal | The evaporator side is not starved. |
| Compressor amps | rAmp | Normal | The compressor is not drawing abnormal current for these pressures. |
| Discharge temperature | rDT | Slightly high | Support signal only — not used to separate the causes. |

### Stage 10 — reasoning down the isolation path

rPwr high → rDP high → rCWL high → condenser water-side problem → steady and worsening over weeks → condenser fouling

The rule path is deterministic and comes from the FDD engine, not from the model. Power is high, so an efficiency fault exists. Discharge pressure is high, so the extra power is being driven by high head. Condenser water leaving is also high, which places the problem on the condenser water side rather than the refrigerant side. The remaining question is which condenser water-side cause: low flow presents as spikes and intermittent behaviour, while fouling presents as a steady drift getting worse over weeks. get_trends shows a steady 3-week drift with no spikes, so the class is condenser fouling. The model’s job here is to explain the path in plain English, not to invent it.

### Stage 11–14 — the grounded answer

Chiller-03 — likely condenser fouling.

Confidence: Likely. All operating gates passed and the pattern has held for 42 minutes.

Chiller-03 is using about 9% more power than normal for its current load and water temperatures.

Head pressure is running high, and the condenser water leaving temperature is also high — so heat is not moving into the condenser water as it should.

The suction side and the compressor look normal, which rules out a starved evaporator and compressor inefficiency.

The pattern has drifted steadily worse over three weeks with no spikes, which points to fouling rather than low condenser flow.

A similar case on Chiller-01 in February was closed by condenser tube cleaning, and power returned to baseline within two days (WO-1877, verified).

Recommended next action: inspect and clean the condenser tubes at the next available window; check the tower water treatment log for the same period.

Offered: create a work order — Prepare draft.

### The same question when the data is not good enough

If the condenser flow signal is invalid or missing, the models that depend on it — discharge pressure, power and condenser water leaving — cannot produce trustworthy residuals. The flows-valid gate fails, and the Copilot must not fall back to a softer version of the same conclusion. It returns:

WHAT THE USER SEES NO_DIAGNOSIS — I cannot diagnose Chiller-03 right now. Three of the six models need a valid condenser flow signal, and that signal is not reporting. Power is elevated, but I cannot tell you why without it. Recommended action: raise a data-quality work order for the condenser flow measurement.

This is the behaviour that makes the rest of the platform trustworthy. A Copilot that guesses when its inputs are missing will eventually send a crew to the wrong equipment, and after that nobody believes the good diagnoses either.

## 3.12 Worked example — act, then prove it worked

### “Create a work order for this.”

| Step | What the Copilot does | Control |
| --- | --- | --- |
| 1 | Carries the resolved asset, fault and evidence pack forward — the user does not re-explain. | Task state |
| 2 | Drafts the WO: asset, fault class, symptom, evidence, recommended work, parts, skills, safety notes. | Validation |
| 3 | Calculates priority from asset criticality, risk, SLA and production impact — and shows the calculation. | Deterministic rule |
| 4 | Checks whether Ravi may create this class of WO on Plant A. | Control Plane |
| 5 | Checks parts: condenser cleaning kit in stock at Plant A stores. | check_part |
| 6 | Shows the complete draft. Nothing has been written yet. | DRAFT mode |
| 7 | On confirmation, calls create_wo with an idempotency key. | Tool gateway |
| 8 | Confirms WO-2291 created, assigned to the mechanical crew, scheduled for Sunday shutdown. | Audit written |
| 9 | Registers a verification task against fault F-8842, due after the work completes. | Task state |

Had this been a safety-critical isolation instead of a cleaning task, step 4 would have returned ALLOW-WITH-APPROVAL, and the Copilot would have shown a prepared request with the named approver rather than a created work order.

### “Did the repair work?”

Six days later the crew has closed out the physical work. The Copilot does not accept “complete” as proof of “fixed”.

| Verification input | What is checked | Result |
| --- | --- | --- |
| Work record | Was the intended work actually performed, with findings recorded? | Tubes cleaned; heavy scale reported |
| Post-work residuals | Have rPwr, rDP and rCWL returned inside the normal band? | All three within band |
| Operating gates | Was the equipment in a valid state when the comparison was made? | PASS |
| Persistence | Has the improvement held across a representative load range? | Held 3 days, 40–85% load |
| Fault state | Has the FDD fault cleared under valid conditions? | F-8842 CLEAR |
| Business outcome | Did the expected energy improvement appear? | About 8% power reduction at like load |

Result: VERIFIED. The Copilot closes the verification task, permits WO-2291 to move to closed, and writes the case into verified-case memory so the next chiller showing the same signature can be matched against a fix that is known to have worked.

If the residuals had not returned to band, the result would be FAIL: the work order reopens, the previous findings are preserved so the next technician does not start from zero, and the fault is re-examined with the new evidence included. If the equipment had not run under comparable conditions, the result would be UNKNOWN — not PASS.

## 3.13 Reports and Work Orders are Copilot skills

Reports and Work Orders remain full products with their own screens. People who prefer to click will keep clicking, and nothing is taken away from them. The change is that the Copilot can reach the same capability, with the same rules, from a sentence — and can chain it to what comes next.

| Capability | Screen still exists? | What the Copilot adds | What the user gains |
| --- | --- | --- | --- |
| Reports | Yes, unchanged | Ask for it, explain it, compare it, drill into it, schedule it. | The report answers a question instead of being one more thing to read. |
| Work Orders | Yes, unchanged | Draft from evidence, price the priority, plan, assign, verify, reopen. | The work order arrives already carrying its own justification. |
| Asset pages | Yes, unchanged | One equipment story instead of eight tabs. | Less hunting across screens. |
| FDD and ML | Yes, unchanged | Explains the rule path and the residuals in plain English. | Existing models finally get used by non-specialists. |
| Knowledge | Yes, unchanged | Retrieves the right procedure at the moment it is needed. | The SOP arrives with the job, not after it. |
| Planning and Inventory | Yes, unchanged | Answers “can we actually do this tomorrow?” in one turn. | Fewer plans that fail on a missing part. |
| Alerts | Yes, unchanged | Groups, explains and ranks instead of listing. | Forty alerts become one problem. |

DESIGN DECISION Reports, Work Orders and the Copilot are not three products. They are one product with three doors, and the Copilot is the door that requires no training.

## 3.14 What the Copilot must never do

| Never | Why it matters | How it is prevented |
| --- | --- | --- |
| Call a write tool without a Control Plane decision. | It would make the model the authority. | The gateway rejects any call without a decision token. |
| Widen its own scope, even to be helpful. | One cross-tenant answer ends enterprise trust. | Scope is recomputed per turn and enforced in the tool, not the prompt. |
| Approve its own action, or act as its own second person. | Approval exists to put a human in the loop. | Approval identity must differ from the requester. |
| State a number it did not retrieve. | An invented number is worse than no number. | The auditor removes any claim not tied to the evidence pack. |
| Treat text inside a document or tool result as an instruction. | This is the main prompt-injection route. | Instruction and data channels are separated; injected text is flagged. |
| Say a repair worked because the work order was closed. | Closure is an administrative act, not proof. | Verification requires post-work evidence under valid gates. |
| Give a diagnosis when the operating gates failed. | It sends crews to the wrong equipment. | Gates run before the rules; failure returns NO_DIAGNOSIS. |
| Issue a control command to plant equipment. | Safety and liability sit with the control system. | No control tool is exposed to the agentic layer at all. |
| Continue silently after a tool failure. | A half-finished action is the worst outcome. | FAILED state reports exactly what was and was not done. |
| Answer a safety question from memory instead of the SOP. | Procedures change and memory does not. | Safety intents force retrieval with the source shown. |

## 3.15 How we will know the Copilot is good

The Copilot is measured before release and continuously afterwards. These are release gates, not dashboards — a build that misses a P0 target does not ship.

| Dimension | Measure | Target | Gate |
| --- | --- | --- | --- |
| Scope safety | Cross-tenant or out-of-scope data appearing in an answer, on the red-team suite. | Zero | P0 |
| Action safety | Unauthorized write attempts that are blocked. | 100% | P0 |
| Grounding | Claims in an answer not supported by the evidence pack. | Under 1% | P0 |
| Honest uncertainty | Cases with failed gates that were answered anyway. | Zero | P0 |
| Intent routing | Routing accuracy on the gold utterance set. | 95% or better | P0 |
| Reference resolution | Correct binding of “this” and “it” on the context test set. | 98% or better | P0 |
| Diagnosis validity | Agreement with the deterministic FDD rule path. | 100% — the model never overrides the rule | P0 |
| Injection resistance | Successful instruction injections through documents or tool results. | Zero | P0 |
| Latency | p95 for a read-only turn; first token. | 8 s; 2 s | P1 |
| Task success | Multi-step tasks completed without the user restarting. | 90% or better | P1 |
| Recommendation value | Recommendations accepted by engineers. | Tracked, rising | P1 |
| Verification quality | Verified repairs that later reopen for the same fault. | Falling | P1 |
| Audit completeness | Material actions with a complete decision trail. | 100% | P0 |

Every one of these is testable before a single customer sees the build. That is the difference between a copilot we can sell to an enterprise and a demo.

# 4. User Flow — What Happens When Someone Uses AI

| Step | What happens in simple English | Example |
| --- | --- | --- |
| 1. User asks | User types or speaks a question/request. | “Why is Chiller-03 unhealthy?” |
| 2. Identify user | Graylinx knows who is asking and their role. | Reliability Engineer |
| 3. Check access | System checks which customer/site/equipment/data the person can see. | Only Plant A assets |
| 4. Understand request | AI decides whether this is a question, report, investigation or action. | Investigation |
| 5. Get information | AI gets the needed equipment data, ML/FDD results, WOs or documents. | FDD + history + SOP |
| 6. Check quality | System checks whether the information is current and good enough. | Valid operating state |
| 7. Answer/explain | AI gives a simple answer and shows supporting proof. | Likely condenser issue |
| 8. Suggest next step | AI offers useful actions. | Inspect condenser / create WO |
| 9. Control action | Before changing anything, rules, risk and approval are checked. | WO approval required |
| 10. Execute | Approved system/tool performs the action. | WO created |
| 11. Verify | Graylinx checks the result after the work. | Fault cleared |
| 12. Record | The action, result and proof are recorded for reports and audit. | Verified repair |

# 5. The Copilot in Practice — Levels and Conversations

## 5.1 Conversational feature levels

| Mode | User experience | Example |
| --- | --- | --- |
| ASK | Get information | “What is happening with my plant?” |
| EXPLAIN | Understand why | “Why is Chiller-03 unhealthy?” |
| INVESTIGATE | Explore evidence | “Compare this fault with the last 5 cases.” |
| RECOMMEND | Get next best action | “What should we inspect first?” |
| DRAFT | Prepare work/report | “Draft a WO and weekly report.” |
| APPROVE | Review controlled action | “Show me what I am approving.” |
| EXECUTE | Perform permitted action | “Create the approved WO.” |
| VERIFY | Check outcome | “Did the repair fix the issue?” |
| REPORT | Generate/summarize report | “Give me the maintenance summary.” |
| ESCALATE | Route to human/team | “Escalate this safety concern.” |

## 5.2 Copilot end-to-end workflow

MESSAGE → IDENTITY → TENANT/SITE/ASSET SCOPE → INTENT → CONTEXT → RISK CLASS → SELECT AGENT → RETRIEVE EVIDENCE → PLAN → POLICY CHECK → APPROVAL IF REQUIRED → TOOL EXECUTION → RESULT VALIDATION → VERIFICATION → RESPONSE → AUDIT

## 5.3 Example conversations

“Show me the worst equipment today.”

Copilot resolves user's site/asset scope → queries health/FDD/risk → ranks assets → shows evidence and reason → offers “Explain”, “Create WO” or “Generate report”.

“Why is this compressor failing?”

Asset context → current equipment readings/ML residuals → FDD gates → historical WOs → relevant SOP → grounded explanation → uncertainty if evidence is insufficient.

“Create a work order for this.”

Copilot identifies the selected fault/asset → summarizes proposed work → checks permission/risk → drafts WO → requests approval if rule requires → creates through WO tool only after authorization.

“Close this WO.”

Copilot checks WO state → verifies required findings and evidence → runs verification → if PASS and user has authority, closure is permitted; otherwise it explains what is missing.

“Give me all customer sites.”

Scope check occurs before retrieval. If user lacks cross-customer permission, the request is denied without exposing data.

## 5.4 Copilot conversations by role

### What the Copilot can do

| Mode | User asks | What Graylinx does |
| --- | --- | --- |
| Ask | “What is the status?” | Finds current allowed information |
| Explain | “Why?” | Explains using supporting data |
| Investigate | “Show me similar cases.” | Searches history and documents |
| Compare | “Which is worse?” | Compares assets/sites/periods |
| Recommend | “What should we do?” | Suggests next steps |
| Draft | “Prepare a WO/report.” | Creates a draft |
| Act | “Create/assign/send.” | Checks rules then uses an approved tool |
| Verify | “Did it work?” | Checks outcome evidence |
| Summarize | “Give me the short version.” | Creates role-specific summary |
| Escalate | “Send this to reliability.” | Routes to the right team |

### Copilot cases by person

| Person | Example question | Expected answer/action |
| --- | --- | --- |
| CEO | “How are we doing?” | Business summary + biggest risks + drill-down |
| Regional Head | “Which site is at risk?” | Site comparison + reasons |
| Plant Manager | “What needs attention now?” | Ranked equipment/work list |
| Maintenance Manager | “Why is backlog high?” | Root causes + suggested actions |
| Reliability Engineer | “Why is this fault happening?” | FDD evidence + similar cases |
| Planner | “What can we schedule tomorrow?” | WOs matched to window/people/parts |
| Technician | “What should I do next?” | Safe procedure + job context |
| EHS | “Is this action allowed?” | Rule/safety result + approval path |
| Customer | “How is my site?” | Customer-scoped performance summary |
| Admin | “Why can't this user access the report?” | Permission/configuration explanation |

# 6. Feature Catalogue at a Glance

| Feature area | What the user can do | Example |
| --- | --- | --- |
| Synex Copilot | Ask, explain, investigate, compare, recommend, draft, act, verify and summarize. | “Why is Chiller-03 unhealthy?” |
| AI Reports | Create, explain, compare, drill down and schedule reports using natural language. | “Give me this week's maintenance summary.” |
| AI Work Orders | Create WOs from chat/Fault Detection and Diagnosis (FDD), summarize, prioritize, plan, assign, assist and verify. | “Create a WO for this fault.” |
| Equipment AI | Ask about any allowed equipment's health, history, faults and repairs. | “Has this happened before?” |
| Reliability AI | Explain FDD/ML findings, find similar cases, trends and repeat failures. | “Why did FDD raise this?” |
| Knowledge AI | Ask manuals, SOPs, previous WOs and approved documents questions. | “What is the inspection procedure?” |
| Planning AI | Suggest what work to do first, when, and who can do it. | “What can we schedule tomorrow?” |
| Parts / Inventory AI | Check parts, reservations, shortages and delivery impact. | “Can we finish this WO tomorrow?” |
| Smart Alerts | Group, explain, prioritize and route important alerts. | “Why did I get this alert?” |
| Technician AI | Give job context, safety guidance, procedures, history and findings capture. | “What should I check first?” |
| Customer AI | Let customers ask about only their sites and equipment. | “How is my plant performing?” |
| Executive AI | Give short business briefings with drill-down. | “What needs my attention?” |
| Verification AI | Check whether work actually fixed the issue. | “Did the repair work?” |
| Safety AI | Explain safety requirements and block controlled unsafe actions. | “Can I perform this action?” |

# 7. Feature Domains in Detail

This section expands the platform from architecture into concrete user-facing features. Each feature is described by purpose, actors, inputs, workflow, example and expected outcome. The three P0 pillars remain the priority: Reports, Work Orders and Synex Copilot.

## 7.1 Feature map

| Priority | Feature domain | Core features | Primary outcome |
| --- | --- | --- | --- |
| P0 | Reports | Dashboards, KPI reports, open more detail, scheduled reports, ad-hoc analysis, AI narrative, exports, comparisons | Understand what is happening |
| P0 | Work Orders | Create, prioritize, approve, assign, execute, parts, findings, verification, close/reopen | Get work done correctly |
| P0 | Synex Copilot | Ask, explain, investigate, recommend, draft, execute, verify, report, escalate | Turn questions into controlled action |
| P0 | Control Plane | Identity, scope, rule, risk, approval, safety, evidence, audit | Make AI safe and controllable |
| P1 | Asset Intelligence | Hierarchy, health, history, dependencies, criticality, digital context | Understand every asset |
| P1 | Reliability / FDD | Fault detection, diagnosis support, evidence, bad actors, trends | Find and explain problems |
| P1 | Knowledge / RAG | SOPs, manuals, cases, WOs, source-aware retrieval | Give grounded answers |
| P1 | Maintenance Planning | Prioritization, scheduling, technician/parts matching, windows | Choose the right work at the right time |
| P1 | Inventory / Procurement | Parts availability, reservation, shortage, reorder/PO suggestions | Remove execution blockers |
| P1 | Alerts / Escalation | Thresholds, FDD events, SLA breaches, risk escalation | Get attention at the right time |
| P1 | Verification / Learning | Post-work validation, reopen, outcome capture, lessons | Prove the fix and improve |
| P2 | Advanced AI | Voice, vision, optimization, deeper autonomy where justified | Extend feature after core loop is reliable |

## 7.2 Feature domains — what Graylinx can deliver

| Domain | New AI feature | What the user gets |
| --- | --- | --- |
| Reports | Ask questions about any report | Answers instead of manual filtering |
| Reports | AI report builder | Create reports from natural language |
| Reports | AI report explanation | Plain-English summary of numbers and changes |
| Reports | Report investigation | Ask why a KPI changed and drill down |
| Reports | Scheduled AI brief | Automatic role-specific daily/weekly summary |
| Work Orders | AI WO creation | Turn a problem or conversation into a structured WO |
| Work Orders | WO summarization | Instant summary of long WO history |
| Work Orders | WO prioritization | Rank work by risk, criticality, SLA and impact |
| Work Orders | WO planning | Suggest technician, time, duration and dependencies |
| Work Orders | WO verification | Check if repair actually fixed the problem |
| Copilot | Synex Copilot | One place to ask, investigate, report and act |
| Copilot | Context-aware assistant | Understands the current screen, asset and user scope |
| Copilot | Multi-turn investigation | Keeps context across follow-up questions |
| Equipment | AI asset assistant | Ask anything about an equipment's health/history |
| Reliability | AI fault explanation | Explain ML/FDD results in simple language |
| Reliability | Similar-case search | Find similar previous faults and repairs |
| Reliability | Bad-actor analysis | Find equipment repeatedly causing problems |
| Knowledge | AI document assistant | Ask questions across manuals, SOPs and site documents |
| Knowledge | Procedure guidance | Show relevant steps with source information |
| Planning | AI maintenance planner | Help decide what work should happen first |
| Inventory | AI parts assistant | Find required parts and possible delays |
| Alerts | AI alert explanation | Explain why an alert matters and what to do |
| Alerts | Smart alert grouping | Combine related alerts and reduce noise |
| Customer | Customer AI assistant | Customer can ask about only their allowed sites |
| Executive | Executive AI briefing | Short business summary with drill-down |
| Technician | Technician AI assistant | Job guidance, history, SOP and findings capture |
| Safety | AI safety assistant | Explain rules and block unsafe actions |
| Learning | AI outcome learning | Use verified repair results to improve future suggestions |
| Governance | AI action control | Every AI action is checked, logged and controlled |

# 8. Reports

## 8.1 Report features

| Feature | What it does | Example |
| --- | --- | --- |
| Executive dashboard | Enterprise/site health at a glance | “Show top 10 risks this month.” |
| Asset report | Health, status, history, criticality | “Give me Chiller-03's last 90 days.” |
| Reliability report | FDD, bad actors, repeat faults, degradation | “Which assets have repeated condenser faults?” |
| Maintenance report | Backlog, PM, MTTR, SLA, workload | “Show overdue critical WOs by site.” |
| Energy report | Consumption, anomalies, savings opportunities | “Which chillers are inefficient?” |
| Cost report | Labor, parts, downtime and avoided cost | “What failures cost us most?” |
| WO report | Lifecycle and verification performance | “How many WOs were reopened after repair?” |
| Comparison | Asset/site/period comparison | “Compare Plant A vs Plant B.” |
| Drill-down | KPI → site → system → equipment → sensor/evidence | “Why did availability drop?” |
| Scheduled report | Role-aware recurring delivery | Monday reliability summary for managers |
| AI narrative | Natural-language explanation over verified metrics | “Summarize the week's maintenance risks.” |
| Export | Controlled PDF/CSV/XLSX or approved destinations | Export monthly customer report |

## 8.2 Report workflow — question to evidence

USER QUESTION → RESOLVE PERSONA/SCOPE → IDENTIFY REPORT/KPI → RETRIEVE AUTHORIZED DATA → QUALITY/FRESHNESS CHECK → CALCULATE → RECONCILE → GENERATE VISUAL/NARRATIVE → SHOW EVIDENCE → DRILL-DOWN / EXPORT / ACTION

## 8.3 Report cases

Case: Executive asks “Are we getting better?”

Copilot selects executive scope → compares current vs prior period → reports availability, MTTR, downtime, cost and repeat failures → highlights material changes → links to affected sites/assets.

Case: Manager asks “Why is Plant A worse?”

Report compares sites → identifies availability/MTTR difference → drills into equipment families → surfaces recurring FDD/WO patterns → offers a ranked action list.

Case: Customer requests monthly report

Customer scope is resolved → approved report template runs → metrics are reconciled → narrative is generated from verified values → recipient authorization is checked → report is delivered and audited.

## 8.4 Report scope, controls and governance

Reports are not static exports. They are a role-aware intelligence surface over the enterprise → asset → sensor hierarchy.

| Report family | Examples | Primary users |
| --- | --- | --- |
| Executive | Enterprise health, risk, availability, cost, downtime, energy, ROI | CXO / Executive |
| Operations | Plant health, production impact, critical assets, alerts | Plant / Operations |
| Maintenance | Backlog, PM compliance, MTTR, SLA, technician workload | Maintenance |
| Reliability | FDD, bad actors, repeat failures, MTBF, degradation | Reliability |
| Energy | Energy performance, anomalies, savings opportunities | Energy |
| Cost | Labor, parts, downtime cost, maintenance spend, avoided cost | Finance |
| WO performance | Open/closed/overdue, SLA, cycle time, verification | Maintenance / Service |
| Customer | Site/asset performance and service outcomes | Customer |
| AI/ML | Model/FDD health, drift, evaluation, AI action outcomes | AI/ML / Governance |

### Report controls

Every report is scoped by customer account → organization → site → asset permissions.

Metrics must have definitions, source lineage, calculation logic and freshness.

Exports and scheduled delivery re-check authorization when executed.

Sensitive data, recipients and external sharing are rule-controlled.

created by AI narrative must remain distinguishable from verified day-to-day facts.

# 9. Work Orders

## 9.1 WO features

| Feature | What it does | Example |
| --- | --- | --- |
| Manual WO | User creates work from observed issue | Technician reports vibration |
| AI-drafted WO | Copilot converts evidence into structured draft | “Create WO for this fault.” |
| Priority | Ranks work by risk/criticality/SLA/context | Critical chiller fault = P1 |
| Approval | Routes controlled actions to allowed approver | Critical repair needs supervisor |
| Planning | Suggests window, technician, duration and dependencies | Schedule during low-load period |
| Assignment | Matches skill, certification, location and availability | Assign HVAC-certified technician |
| Parts | Checks stock, reservation and shortage | Reserve compressor seal kit |
| Execution | Technician follows safe procedure and records work | Inspection → repair → findings |
| Evidence | Attach readings, photos, notes, documents | Before/after measurements |
| Verification | Checks whether equipment returned to expected behavior | FDD clears after repair |
| Reopen | Automatically/manual reopen when repair fails | Fault persists after repair |
| Escalation | Routes unresolved/high-risk work | Escalate to OEM/EHS |
| Closure | Controlled final state | Verified + accepted + audited |

## 9.2 WO workflow cases

Case A — FDD creates maintenance opportunity

FDD detects continues for the required time abnormality → evidence pack created → Reliability Agent explains → Maintenance Agent proposes action → WO draft → rule checks risk → approval if required → planned → assigned → executed → verified.

Case B — Technician creates WO from field observation

Technician says “Chiller-03 has abnormal noise” → Copilot resolves asset → asks/records structured observation → checks history → creates WO → supervisor receives notification if priority threshold is met.

Case C — Parts unavailable

WO requires part → Inventory Agent checks stock → part unavailable → procurement suggestion → ETA evaluated against maintenance window → planner reschedules or escalates.

Case D — Repair did not work

WO marked complete → verification sees abnormality remains → verification FAIL → WO reopens → previous findings preserved → next diagnosis begins.

## 9.3 Work order non-negotiables

The WO system is Graylinx's controlled execution loop.

MASTER WO FLOW DETECT → DIAGNOSE → RECOMMEND → DRAFT → APPROVE → PLAN → ASSIGN → PARTS → EXECUTE → FINDINGS → REPAIR → VERIFY → CLOSE / REOPEN → LEARN

| State | Allowed transition | Required control |
| --- | --- | --- |
| DRAFT | → APPROVAL / CANCEL | Permission + payload validation |
| APPROVAL | → APPROVED / REJECTED / EXPIRED | Authorized approver |
| APPROVED | → PLANNED | Planning rule |
| PLANNED | → ASSIGNED | Skill + availability + scope |
| ASSIGNED | → IN_PROGRESS | Technician authorization |
| IN_PROGRESS | → COMPLETED | Findings + work record |
| COMPLETED | → VERIFIED / VERIFICATION_PENDING | Evidence-based verification |
| VERIFIED | → CLOSED | Closure rule |
| VERIFIED | → REOPENED | Failed/uncertain outcome |
| ANY CONTROLLED STATE | → ESCALATED | Safety, SLA, failure or rule event |

### WO non-negotiables

Completion is not automatically successful repair.

Critical work requires the defined approval/safety path.

All writes are idempotent and two people/processes changing the same thing at once-safe.

AI cannot bypass state transitions.

Verification failure can reopen the WO.

Every important state/action is auditable.

# 10. Equipment and Asset Intelligence

| Capability | Function | Example |
| --- | --- | --- |
| Hierarchy | Enterprise → Site → Plant → System → Equipment → Component → Sensor | Navigate from enterprise risk to a valve |
| Asset profile | Identity, make/model, criticality, age, status, owner | Open Chiller-03 profile |
| Health | Current health + trend + risk | Health deteriorating over 14 days |
| History | WOs, faults, readings, interventions | Show last 12 repairs |
| Dependencies | Upstream/downstream relationships | Which systems depend on this pump? |
| Criticality | Business/safety/production importance | Criticality = high |
| Similar assets | Compare peers | Compare Chiller-03 with Chiller-01/02 |
| Context | Current operating state and maintenance window | Running at 85% load |

Asset workflow: SELECT ASSET → LOAD AUTHORIZED CONTEXT → HEALTH → HISTORY → DEPENDENCIES → FDD → KNOWLEDGE → RECOMMENDATION → ACTION.

# 11. What Is ML, What Is Rules, What Is the LLM

Graylinx now contains three very different kinds of intelligence, and they do three very different jobs. If a reader cannot tell them apart, they will assume the language model is diagnosing the equipment. It is not, and it never will. This short chapter draws the line, because almost every question an engineer, an auditor or a customer asks about the platform turns out to be this question.

## What is deciding what

There are four kinds of software in the platform. Only one of them is allowed to be uncertain.

| Kind | What it does | How it decides | Can it be wrong? |
| --- | --- | --- | --- |
| Plain software | Stores records, moves work orders through their states, checks who is allowed to do what, keeps the audit trail. | Fixed code. The same input always produces the same output. | Only if it has a bug — never by design. |
| Deterministic rules | Operating gates, the fault isolation path, priority calculation, approval routing, verification pass or fail. | Written rules over measured values. Auditable line by line. | Only if the rule itself is wrong — and then it is wrong the same way every time, so it can be found and fixed. |
| Machine learning | Predicts what each signal should read when the equipment is healthy, so we can measure how far reality has moved away from it. | Models trained on the equipment’s own normal behaviour. | Yes — within a known error band, and only inside the operating range it was trained on. This is why gates and drift checks exist. |
| The LLM / agentic layer | Understands the question, plans which tools to call, explains the result in plain English, drafts the work order. | Language reasoning over evidence that other layers produced. | Yes — which is exactly why it is never the thing that names a fault or grants a permission. |

## Who decides what — the full split

| Question | Decided by | Never decided by |
| --- | --- | --- |
| Is this reading abnormal, and by how much? | The ML model, as a residual | Rules or the LLM |
| Is the equipment in a fit state to be judged at all? | A deterministic gate | ML or the LLM |
| Has the pattern lasted long enough to be a fault? | A deterministic persistence rule | The LLM |
| Which fault class is this? | The deterministic FDD isolation path over the residuals | The LLM |
| How confident should we be? | The gate results plus the rule path | The LLM’s tone |
| What does all this mean in plain English? | The LLM | — |
| What should we do about it? | The LLM proposes; deterministic rules rank it; a human decides | The LLM alone |
| What priority number does this work get? | A deterministic formula over criticality, risk, SLA and production impact | The LLM |
| Is this person allowed to do this? | Plain software — the Control Plane | ML or the LLM |
| Did the repair actually work? | Post-work residuals judged by a deterministic verification rule | The technician’s note alone, or the LLM |
| What words does the user finally read? | The LLM, checked against the evidence pack | — |

THE RULE THAT KEEPS THIS HONEST The language model never invents a diagnosis. The FDD engine produces the rule path; the language model reads that path and explains it. If the rule path ends in NO_DIAGNOSIS, the language model says NO_DIAGNOSIS — it is not permitted to soften it into a guess.

## What the ML actually does, in plain English

Graylinx does not train models to recognise faults. It trains models to predict what healthy equipment should be doing right now, given the conditions it is working under. The gap between prediction and reality is the residual, and the residual is the signal everything else reasons about.

What the model expected  −  what actually happened  =  the residual

This is done deliberately. A plant produces enormous amounts of normal running data and very little fault data, and every fault looks slightly different. Modelling normal is therefore both more accurate and more transferable than trying to learn each fault directly — and it means a fault the platform has never seen before still shows up as an abnormal residual.

## What the ML cannot do

Stating this plainly is what makes the rest of the platform credible.

It cannot explain itself — A residual says a reading is abnormal. It does not say why. The rules do that.

It cannot work outside its envelope — outside the load and temperature range a model was trained on, its prediction is not trustworthy and its residual must not be used.

It cannot replace a sensor — if a required input signal is missing or invalid, the models that depend on it stop producing usable output. No amount of AI compensates for an instrument that is not reporting.

It cannot separate what the sensors cannot separate — some causes look identical through the available instruments. Refrigerant undercharge and an expansion-valve restriction cannot be cleanly separated with this sensor set, so the platform labels them together and says so rather than picking one.

It can go quietly stale — if the equipment, the control strategy or the duty changes, a model slowly becomes wrong without announcing it. This is why model health and drift are monitored continuously, and why a failing model is taken out of service rather than left to mislead people.

## Where each kind lives

| Layer | Kind of software | Produces |
| --- | --- | --- |
| Data and digital twin | Plain software | Clean, timestamped, hierarchy-aware signals |
| Equipment ML | Machine learning | Predictions and residuals with validity flags |
| FDD and reliability | Deterministic rules | Gates, persistence, fault class, confidence |
| Knowledge and retrieval | Retrieval plus the LLM | Sourced answers from approved documents |
| Copilot and agents | The LLM | Understanding, explanation, plans, drafts |
| Control Plane | Plain software | Allow, approve, deny — and the audit record |
| Execution and workflow | Plain software | Work orders, states, notifications, schedules |

# 12. Reliability and Fault Detection

| Capability | Function | Example |
| --- | --- | --- |
| Detection | Detect abnormal residual/behavior | Power residual outside normal band |
| Operating gates | Only evaluate when equipment state is valid | Compressor ON + stable load |
| Persistence | Reject transient spikes | Fault persists 10 min |
| Volatility | Detect unstable behavior | Pressure oscillation |
| Trend | Detect deterioration | Residual worsening over 7 days |
| Fault ranking | Rank plausible issues | Condenser performance most likely |
| NO_DIAGNOSIS | Explicitly decline when evidence is insufficient | “Insufficient evidence” |
| Evidence pack | Make conclusion inspectable | Residuals + gates + history |
| Bad actor | Find repeat/poor performers | Repeated fault across 5 cycles |
| Verification | Check post-repair state | Residual returns to normal |

## 12.1 Reliability case

Telemetry → ML residuals → operating-state gate → persistence/volatility/trend → FDD decision → evidence pack → Reliability Agent explanation → maintenance suggestion → WO → post-work equipment readings → verification.

## 12.2 RELIABILITY AI

| Feature | Example | Value |
| --- | --- | --- |
| Fault explanation | “Why did FDD raise this?” | Makes ML useful to non-ML users |
| Fault ranking | “What is most likely?” | Focuses investigation |
| Similar cases | “Has this happened before?” | Reuse proven experience |
| Repeat failure | “Which assets keep failing?” | Find systemic problems |
| Trend explanation | “Is this getting worse?” | Early attention |
| Bad actor list | “Who causes most downtime?” | Focus maintenance effort |
| Confidence/uncertainty | “How sure are we?” | Avoids false certainty |
| NO_DIAGNOSIS | Not enough proof | Prevents unsafe/false conclusions |

# 13. Knowledge and Document Intelligence

| Knowledge source | Use | Example |
| --- | --- | --- |
| SOP | Step-by-step procedure | Condenser inspection SOP |
| Manual | Manufacturer technical information | Compressor service manual |
| Historical WO | What was done before | Previous vibration repair |
| Verified case | Known-good troubleshooting pattern | Similar fault on Chiller-07 |
| Asset documentation | Site-specific configuration | BMS point mapping |
| Policy | Operational restrictions | Approval rule |
| Safety document | Safety requirements | Permit/LOTO procedure |

RAG workflow: QUERY → AUTHORIZE SCOPE → RETRIEVE → RANK → CHECK SOURCE/FRESHNESS → GROUND → ANSWER WITH CITATIONS/EVIDENCE → AUDIT.

Retrieved content cannot override system rule or safety.

Conflicting sources should be surfaced rather than silently merged.

Unverified generated content should not automatically become trusted knowledge.

# 14. Planning, People and Inventory

| Capability | Case | Workflow |
| --- | --- | --- |
| Prioritization | Many WOs compete for same window | Risk + criticality + SLA + production + parts + skills → ranked queue |
| Scheduling | Maintenance window tomorrow | WO duration + asset dependency + production schedule → suggested slot |
| Assignment | Need qualified technician | Skills + certification + availability + location → candidates |
| Parts | Part not in stock | Required part → stock/ETA → reserve/order/substitute → schedule decision |
| Vendor/OEM | Internal team cannot perform work | Qualification + contract + SLA → vendor escalation |
| Shift handover | Unfinished critical WO | State + findings + risk → next shift briefing |

## 14.1 Planning example

Three critical WOs compete for one maintenance window. Planning Agent evaluates asset criticality, risk, production impact, technician certification, parts availability and expected duration. It recommends an order; the planner approves; the system schedules and records the decision. The agent cannot override a safety or authorization constraint.

## 14.2 PLANNING, INVENTORY AND ALERT AI

| Feature | Case | AI help |
| --- | --- | --- |
| Priority ranking | 30 WOs, 5 technicians | Rank by risk, criticality, SLA, production and dependencies |
| Schedule suggestion | Tomorrow has a 4-hour maintenance window | Fit the best WOs into the window |
| Technician matching | Need certified HVAC technician | Match skill, certification, location and availability |
| Parts prediction | Repeated pump repair | Warn that a common part may be needed |
| Shortage warning | Critical WO has no part | Tell planner before scheduling |
| Alert explanation | “Why did I get this alert?” | Explain trigger and impact |
| Alert grouping | 20 related sensor alerts | Group into one useful event |
| Escalation | Critical fault not acknowledged | Route to next responsible person |

# 15. Alerts and Escalation

| Alert type | Trigger | Action |
| --- | --- | --- |
| Equipment fault | FDD continues for the required time fault | Notify reliability/maintenance; offer WO |
| Critical risk | Risk crosses threshold | Immediate escalation per rule |
| SLA breach | WO approaching/overdue | Notify owner/manager; reprioritize |
| Data quality | Sensor/model input invalid | Suppress unsafe diagnosis; open data-quality path |
| AI anomaly | Agent/tool behavior abnormal | Observe, contain, disable/rollback if required |
| Safety | Safety condition detected | Stop/deny controlled action and route to allowed human |

Escalation workflow: EVENT → CLASSIFY → DEDUPLICATE → SCOPE → PRIORITY → ROUTE → ACKNOWLEDGE → ACT → VERIFY → CLOSE/ESCALATE.

# 16. Verification and Learning

| Verification | Evidence | Outcome |
| --- | --- | --- |
| Telemetry verification | Post-work readings/residuals | PASS / FAIL / UNKNOWN |
| Technician verification | Checklist/findings | PASS / FAIL |
| Supervisor acceptance | Review of critical work | ACCEPT / REWORK |
| FDD verification | Fault clears under valid operating conditions | CLEAR / PERSIST |
| Business verification | Downtime/energy/reliability outcome | Outcome measured |

## 16.1 Learning workflow

OUTCOME → CAPTURE HUMAN OVERRIDE/RESULT → CLASSIFY SUCCESS/FAILURE → UPDATE CASE LIBRARY → EVALUATE FDD/AGENT/POLICY → CONTROLLED CHANGE → validation → APPROVAL → RELEASE.

Do not automatically retrain from a single user correction.

Human feedback becomes a governed signal.

Production changes require evaluation and rollback feature.

# 17. Customer, Executive and Technician Experiences

| Experience | New AI feature | Example |
| --- | --- | --- |
| Customer | Ask about site performance | “Why did my site's availability fall?” |
| Customer | Ask about open work | “What work is planned for this week?” |
| Customer | Report explanation | “Summarize this month's issues.” |
| Executive | Daily business briefing | “What needs my attention?” |
| Executive | Risk explanation | “Why is this site high risk?” |
| Executive | Decision support | “Where should we spend maintenance budget?” |
| Technician | Job briefing | “Give me the important points before I start.” |
| Technician | Live guidance | “What should I check next?” |
| Technician | Voice/text findings | “Bearing is worn and noisy.” |
| Technician | Close-out summary | AI creates a clean work summary from findings. |

# 18. Safety — Help, Never Bypass

| Case | AI behavior |
| --- | --- |
| User asks for unsafe action | Block or route to authorized human |
| Permit required | Show permit requirement and approval path |
| Technician lacks required qualification | Do not authorize controlled action |
| Document conflicts with safety rule | Safety rule wins; show the conflict |
| Emergency | Use defined emergency workflow; record who approved what |

Simple rule: AI can explain safety requirements, prepare work and help people follow procedures. AI must not secretly bypass safety controls.

# 19. Cases — How the Features Work Together

## Case 1 — Manager Finds Today's Important Problems

User: “What needs attention today?”

Flow: Copilot checks the manager's allowed sites → checks equipment health, FDD events, critical WOs and SLA risks → ranks the important items → explains each item → offers actions.

Result: Manager gets a short prioritized list instead of checking many screens.

## Case 2 — Fault Becomes a Work Order

User: “Create a WO for this Chiller-03 fault.”

Flow: AI understands the selected equipment → collects the fault and supporting data → prepares WO details → checks permission/risk → asks for approval if required → creates the WO.

Result: A useful, evidence-backed WO is created with less manual typing.

## Case 3 — Technician Gets Help

User: “What should I check first?”

Flow: AI reads the current WO and equipment context → finds the approved procedure → shows the first safe checks → records the technician's findings.

Result: The technician gets job-specific help without searching many documents.

## Case 4 — Repair Is Verified

User: “Did the repair fix the problem?”

Flow: After the WO is completed → system checks new equipment readings and FDD state → compares before/after → decides PASS, FAIL or not enough information.

Result: A WO is not called successful just because someone clicked Complete.

## Case 5 — Executive Wants the Business Story

User: “How are we doing this month?”

Flow: AI builds a role-appropriate summary → shows availability, downtime, cost, major risks and critical work → lets the executive ask why any number changed.

Result: Leadership gets the business answer first and can drill into technical detail only when needed.

## Case 6 — Customer Wants a Site Report

User: “Why did my site's performance drop?”

Flow: Customer scope is checked → AI analyzes allowed site data → explains the main drivers → links to relevant equipment and WOs → keeps other customers' data hidden.

Result: Customer receives a clear, scoped explanation.

## Case 7 — Not Enough Evidence

User: “What exactly failed?”

Flow: ML/FDD data is checked → operating conditions are invalid or evidence conflicts → AI does not invent a diagnosis → explains what is missing and suggests the next data/check needed.

Result: The platform is useful without pretending to know something it cannot prove.

## Case 8 — Many Alerts Are Really One Problem

User: “Why am I getting so many alerts?”

Flow: System groups related alerts → finds the common equipment/event → explains the main issue → sends the appropriate alert instead of repeating the same message.

Result: Less alert noise and faster attention to the real issue.

## 19.1 Complete Example — Fault → Fix → Proof → Report

1. Existing ML/FDD detects abnormal equipment behavior.
2. Graylinx checks that the equipment is in a valid operating state and the issue persists.
3. Reliability AI explains the finding using the available proof.
4. User asks the Copilot what to do.
5. AI suggests the next inspection or repair.
6. User asks AI to prepare a WO.
7. Control checks permission, risk and approval.
8. WO is planned and assigned.
9. Technician performs the work and records findings.
10. Graylinx checks the equipment after repair.
11. PASS → close. FAIL → reopen/escalate. UNKNOWN → request more evidence.
12. Verified result becomes part of the report/history and future learning.

# 20. End-to-End Business Cases

| Case | Actors | End-to-end flow | Success measure |
| --- | --- | --- | --- |
| Executive risk review | Executive + Copilot | Ask → report → open more detail → top risks → actions | Decision time reduced |
| Plant health review | Plant Manager + Reliability | Dashboard → bad actors → evidence → action plan | Risk/backlog reduced |
| Predictive maintenance | FDD + Reliability + Maintenance | Detect → diagnose → WO → repair → verify | Failure/downtime avoided |
| Technician guided repair | Technician + Copilot | WO → safety → SOP → parts → repair → verify | MTTR / first-time-fix |
| Customer monthly review | Customer + Service | Report → explain → open more detail → actions | Customer transparency |
| Critical safety issue | EHS + Maintenance | Alert → block → human review → permit → controlled work | No unsafe execution |
| Repeated failure | Reliability + Maintenance | Pattern detection → case comparison → corrective action → verification | Repeat failure reduction |
| Bad data | Data/IoT + Reliability | Quality fail → NO_DIAGNOSIS → data action → recheck | False diagnosis reduction |
| AI rule incident | Security/Governance | Detect → contain → audit → investigate → rollback | Incident MTTR |

# 21. Role-Based Examples

| User | Example question | Main experience |
| --- | --- | --- |
| Executive | “What are the biggest risks?” | Short business summary + drill-down |
| Plant Manager | “What needs attention now?” | Prioritized equipment/work list |
| Maintenance Manager | “Why is backlog high?” | WO blockers + actions |
| Reliability Engineer | “Why did FDD trigger?” | ML/FDD evidence + similar cases |
| Planner | “What can we schedule tomorrow?” | WO + people + parts + time window |
| Technician | “What do I check first?” | WO + SOP + safety + history |
| EHS | “Is this action allowed?” | Safety/rule/approval result |
| Customer | “How is my site?” | Customer-scoped report and explanation |
| Admin | “Why can't this user access it?” | Permission/configuration explanation |

# 22. What Is New in Graylinx — Product Positioning

| Area | Traditional system | New Graylinx AI experience |
| --- | --- | --- |
| Reports | Open dashboard and filter | Ask a question and get a grounded answer |
| Work Orders | Manually create and manage | AI prepares, explains, prioritizes and verifies |
| Equipment | Open many screens | Ask the equipment directly |
| FDD | Technical fault output | Simple explanation + proof + next action |
| Knowledge | Search documents | Ask questions across approved knowledge |
| Planning | Planner manually compares many factors | AI suggests the best options |
| Alerts | Many separate notifications | AI groups, explains and prioritizes |
| Customers | Static reports | Interactive customer AI assistant |
| Executives | Many dashboards | Short AI briefing + drill-down |
| Technicians | Manual searching and writing | Job-aware AI guidance and structured findings |
| Verification | Often manual closure | AI helps prove whether the repair worked |
| Platform control | Rules spread across systems | Central AI Control Plane |

# 23. Product Rules for Every New AI Feature

Make the user task easier, not more complicated.

Use existing Graylinx data and ML as the foundation.

Show the reason/proof for important AI answers.

Never invent a diagnosis when the evidence is not enough.

Never let AI bypass access, safety or approval rules.

Let users move from answer → detail → action without losing context.

For actions, show what will happen before it happens when approval is required.

Always verify important maintenance outcomes.

Keep a record of important AI decisions and actions.

# 24. Delivery Priorities and Roadmap

| Phase | Build first | Reason |
| --- | --- | --- |
| P0.1 | Reports foundation + KPI/lineage + role scope | Core visibility |
| P0.2 | WO lifecycle + state machine + approvals | Core execution |
| P0.3 | Synex Copilot read/analyze/report | Fastest broad user value |
| P0.4 | Copilot → governed WO draft/create | Close intelligence-to-action loop |
| P0.5 | FDD → evidence → suggestion → WO | Predictive maintenance loop |
| P0.6 | Post-work verification → reopen/close | Prove outcomes |
| P1 | Planning + inventory + vendor + alerts | Operational depth |
| P1 | Advanced RAG/knowledge workflows | Better grounded assistance |
| P2 | Voice/vision/advanced autonomy | Only after core controls and outcomes are proven |

NORTH-STAR: Every feature should answer one of four questions: What is happening? Why? What should we do? Did it work?

## 24.1 FEATURE PRIORITY — WHAT WE SHOULD BUILD FIRST

| Priority | Feature group | Why |
| --- | --- | --- |
| P0 | Copilot read + report assistant | Fastest way to make the platform easier to use |
| P0 | Reports + natural-language questions | Core business objective |
| P0 | WO creation + summarization | Core operational objective |
| P0 | FDD explanation + evidence | Connect existing ML to users |
| P0 | WO verification | Close the loop |
| P0 | AI Control Plane | Make all new AI features safe |
| P1 | Planning + technician assistance | Make execution smarter |
| P1 | Knowledge/document assistant | Ground answers in company knowledge |
| P1 | Inventory/parts assistant | Remove maintenance delays |
| P1 | Customer and executive assistants | Extend value to every level |
| P1 | Smart alerts | Reduce noise and improve response |
| P2 | Voice, vision and deeper automation | Add after the core loop is reliable |

# 25. Product North Star

Graylinx should feel like one intelligent maintenance assistant for the whole organization: from the executive asking a business question, to the reliability engineer investigating a fault, to the technician fixing the equipment.

The AI should make existing Graylinx data, ML and workflows easier to understand and use — and then connect them into a controlled loop:

ASK → UNDERSTAND → FIND PROOF → EXPLAIN → RECOMMEND → APPROVE → WORK → VERIFY → REPORT → LEARN

# PART TWO

Architecture & Engineering

How the product above is built, controlled, secured, tested, operated and governed — from agents and tools to the Control Plane and release gates.

# 26. Executive Product Definition

THE PRODUCT IN ONE LINE Graylinx is an AI-native maintenance and reliability platform centered on Reports, Work Orders and an Synex Copilot, using existing equipment intelligence to turn evidence into controlled action and verified outcomes.

## 26.1 Priority hierarchy

| Priority | What belongs here | Purpose |
| --- | --- | --- |
| P0 — Core product | 📊 Reports; 🔧 Work Orders; 🤖 Synex Copilot | What customers directly use and value. |
| P0 — Trust foundation | AI Control Plane; Identity; Scope; Policy; Safety; Approval; Evidence; Audit | What makes the core product safe and enterprise-grade. |
| P1 — Intelligence foundation | Existing ML; FDD; RAG; Asset hierarchy; Data quality | Makes the core experiences intelligent and grounded. |
| P1 — Execution support | Planning; Scheduling; Inventory; People; Notifications; Integrations | Makes WOs and decisions executable. |
| P2 — Advanced features | Voice, vision, deeper autonomy, advanced optimization | Add only when a measurable business case exists. |

KEY PRODUCT PRINCIPLE Do not let 'AI that can plan and use tools AI' become the product. Agentic AI is the execution mechanism underneath the three core customer experiences.

## 26.2 High-level to low-level design

| Level | Question answered | Typical artifacts |
| --- | --- | --- |
| L0 — Business | Why does Graylinx exist? | Objectives, value proposition, ROI |
| L1 — Product | What do users experience? | Reports, WOs, Copilot, menus, user roles |
| L2 — Workflow | How does a job move end-to-end? | Journey maps, workflow/state diagrams |
| L3 — Architecture | What components make it work? | Layered architecture, service boundaries |
| L4 — Control | Who/what is allowed to act? | RBAC/ABAC, rule, risk, approval, safety |
| L5 — Engineering | How exactly is it implemented? | API/tool contracts, schemas, state machines |
| L6 — Verification | How do we prove it works? | validation, test matrix, service targets, audit evidence |

# 27. Personas and Role Architecture

Use many business user roles, but implement shared user role families and configurable permissions—not 30+ independent products.

| Family | Personas |
| --- | --- |
| Business | CXO/Executive; Asset Owner; Regional Head; Finance/Cost Manager |
| Operations | Plant Manager; Operations Manager; Production/Business Operations Manager |
| Maintenance / Service | Maintenance Manager; Reliability Manager; Supervisor; Planner; Technician; Service Manager; Contractor; OEM Engineer |
| Engineering / Intelligence | Reliability Engineer; Controls/BMS Engineer; Energy Manager; Data/IoT Engineer; AI/ML Engineer; Data/Reliability Analyst; AI Governance/Product Owner |
| Supply Chain | Inventory/Stores Manager; Procurement/Buyer; Vendor/AMC Manager |
| Safety / Governance | EHS/Safety; Auditor/Compliance; Configuration/Change Manager |
| Platform | System Administrator; Integration/IT Administrator |
| Customer | Customer Administrator; Customer Manager; Customer Viewer |

## 27.1 Authorization model

PERSON → ROLE → TENANT → ORGANIZATION/SITE → ASSET SCOPE → DATA SCOPE → ACTION SCOPE → APPROVAL AUTHORITY

ROLE ≠ PERMISSION A Reliability Engineer may have access to Plant-01 but not Plant-03. A Technician may edit assigned WOs but not close critical work. Authorization must be evaluated at the API/tool boundary, not only in the UI.

# 28. Enterprise Architecture — High Level

| Layer | Name | Primary responsibility |
| --- | --- | --- |
| L0 | Physical / OT | Equipment, sensors, PLC, BMS, SCADA and field environment |
| L1 | Connectivity / Integration | Gateways, protocols, APIs, CMMS/ERP/BMS integrations |
| L2 | Data / Digital Twin | Telemetry, asset hierarchy, master data, quality, lineage |
| L3 | Equipment ML | Existing models, health, anomaly, degradation, residuals |
| L4 | FDD / Reliability | Operating gates, persistence, volatility, trends, deterministic fault evidence |
| L5 | Knowledge / RAG | SOPs, manuals, historical WOs, verified cases, customer account-scoped retrieval |
| L6 | Agentic Intelligence | Copilot, orchestrator, specialized agents, task planning |
| L7 | AI Control Plane | Identity, scope, risk, rule, safety, approval, tools, evidence, audit |
| L8 | Execution / Enterprise | WO/CMMS, scheduling, inventory, procurement, notifications, reports |
| L9 | Verification / Learning | Post-work evidence, outcome, feedback, controlled learning, ROI |
| Cross-cutting | Security / Governance | Zero Trust, privacy, resilience, compliance, supply chain and lifecycle governance |

## 28.1 High-level product flow

USER → REPORTS / WOs / COPILOT → CONTROL PLANE → AGENTS → TOOLS → ML/FDD/RAG/DATA → EVIDENCE → POLICY/APPROVAL → EXECUTION → VERIFICATION → AUDIT → OUTCOME

# 29. Agentic and Model Architecture

Keep the current four-model local configuration as the baseline unless evaluation demonstrates a need for change.

| Model | Role | Primary responsibility |
| --- | --- | --- |
| gemma4:26b-a4b-it-qat | Brain | Reasoning + final answer |
| devstral:latest | Tool executor | ReAct loop + NL→SQL |
| phi4 | Text / auditor / router / RAG | Narration, auditing, routing arbitration, RAG and grounding |
| nomic-embed-text | Embeddings | Local 768d embeddings |

## 29.1 Agent families

| Agent | Core job | Hard boundary |
| --- | --- | --- |
| Orchestrator | Coordinate workflow and state | Cannot bypass rule |
| Asset | Asset context and health | Asset scope only |
| Reliability | ML/FDD evidence and diagnosis support | Must use evidence |
| Maintenance | Maintenance suggestion and WO drafting | Cannot bypass safety |
| WO | Controlled WO operations | Tool gateway required |
| Knowledge/RAG | Authorized knowledge retrieval | Tenant/source scoped |
| Planning | Schedule/assignment suggestion | Cannot override skills/safety |
| Inventory | Parts availability/reservation suggestion | Financial thresholds enforced |
| Verification | Repair outcome determination | Evidence required |
| Reporting | Role-aware report generation | No scope expansion |

## 29.2 Agent registry

Each production agent must register: owner, purpose, version, prompt/instruction version, allowed tools, allowed data scopes, risk class, evaluation suite, service target, rollback version and status.

# 30. The Equipment ML Layer — Inventory, Lifecycle and Trust

The equipment ML layer existed before the AI layer and is not replaced by it. It produces the numeric signals that the FDD rules classify, the Copilot explains and the verification step re-measures. This chapter defines it as a governed asset with an inventory, a lifecycle, a health standard and a trust contract.

## Model inventory — water-cooled chiller

Six normal-operation models per chiller. Each predicts one signal from the conditions the machine is actually working under, and each yields one residual.

| Model | Predicts | Inputs | Residual |
| --- | --- | --- | --- |
| Model DP | Discharge pressure | Suction pressure; chiller cooling load; condenser water entry temperature; condenser flow; compressor lead/lag | rDP |
| Model SP | Suction pressure | Evaporator leaving temperature; evaporator entry temperature; evaporator flow / DPT; compressor lead/lag | rSP |
| Model DT | Discharge temperature | Suction pressure; discharge pressure; chiller cooling load; condenser water entry temperature; condenser flow; compressor lead/lag | rDT |
| Model Power | Chiller amps / power | Evaporator leaving temperature; chiller load; condenser water entry temperature; condenser flow | rPwr |
| Model Compressor Amps | Compressor amps | Suction pressure; discharge pressure; chiller load; compressor lead/lag | rAmp |
| Model Condenser Leaving | Condenser water leaving temperature | Chiller load; condenser water entry temperature; condenser flow; compressor lead/lag | rCWL |

Residual definition: rX(t) = X_actual(t) − X_predicted(t), where the prediction comes from the normal-operation model for that signal.

## Sensor and tag requirements

| Signal | Required for | Notes |
| --- | --- | --- |
| Suction pressure, discharge pressure, discharge temperature | Models DP, SP, DT, Compressor Amps | Core refrigerant-side instrumentation |
| Compressor amps | Model Compressor Amps | Compressor current or equivalent |
| Chiller power | Model Power | External energy meter where present; otherwise the chiller kW estimate |
| Evaporator entering and leaving water temperature | Models SP, Power; evaporator ΔT | Also drives the chilled-water ΔT health check |
| Condenser entering and leaving water temperature | Models DP, DT, Power, Condenser Leaving; condenser ΔT | Water-cooled machines |
| Evaporator flow / DPT | Model SP; efficiency proxy | Primary variable installations |
| Condenser flow | Models DP, DT, Power, Condenser Leaving; efficiency proxy | The highest-leverage single measurement in this set |
| Compressor lead/lag state | Models DP, SP, DT, Compressor Amps, Condenser Leaving | Staging context; without it residuals shift at every stage change |
| Wet bulb temperature | Cooling tower assessment | Water-cooled machines |
| Outside air temperature | Air-cooled equivalents | Air-cooled machines |

### Computed parameters

Evaporator ΔT = evaporator entering − evaporator leaving

Condenser ΔT = condenser leaving − condenser entering

Efficiency proxy = (condenser ΔT × condenser flow) ÷ (evaporator ΔT × evaporator flow)

## Input dependency map

This table is the most operationally important one in the chapter. It states, in advance, exactly what the platform loses when a given signal fails — and therefore what the Copilot is obliged to say instead of guessing.

| If this signal is missing or invalid | Models affected | What is lost | Platform behaviour |
| --- | --- | --- | --- |
| Condenser flow | DP, DT, Power, Condenser Leaving — four of six | The entire efficiency and high-head branch: rPwr, rDP and rCWL all become untrustworthy, so condenser water-side, refrigerant-side high head and compressor inefficiency can no longer be separated. | NO_DIAGNOSIS for those classes; raise a data-quality work order for the condenser flow measurement. |
| Evaporator flow / DPT | SP | rSP becomes untrustworthy, so starved evaporator and expansion-valve hunting cannot be assessed. | NO_DIAGNOSIS for evaporator-side classes. |
| Chiller power | Power | The efficiency symptom that starts the whole isolation path disappears. | No efficiency fault can be raised at all. |
| Compressor lead/lag | DP, SP, DT, Compressor Amps, Condenser Leaving | Residuals shift at every staging change and produce false abnormalities. | Gate fails on staging transitions; persistence window extended. |
| Condenser water entry temperature | DP, DT, Power, Condenser Leaving | Head-pressure behaviour cannot be normalised for the water conditions. | NO_DIAGNOSIS for condenser-side classes. |
| Any temperature or pressure sensor drifting | The models using it | A biased input produces a confident but wrong residual. | Sensor-bias checks run first; a suspected sensor fault is reported as a sensor fault, not an equipment fault. |

OPERATING PRINCIPLE Rule out instrumentation before dispatching a crew. A residual that is abnormal only because its input is wrong looks identical to a real fault — the sensor-bias checks exist precisely to separate the two, and they run before any dispatch recommendation is offered.

## Training and baseline

| Aspect | Standard |
| --- | --- |
| What is trained | Normal behaviour only. Known fault periods and known bad-data periods are excluded from the training window. |
| Baseline source | The commissioning baseline where one exists; otherwise a verified healthy period agreed with the site. |
| Minimum window | Enough continuous running to cover the machine’s real duty, not simply a fixed number of days. |
| Envelope coverage | The training set must span the load range and the water temperature range the machine actually operates in. Coverage is recorded with the model. |
| Per-asset, not per-fleet | Models are fitted per chiller. Two identical machines on the same site do not share a model. |
| Recorded with the model | Training window, excluded periods, envelope, error band, fit statistics and the engineer who approved it. |

## Model health, drift and quarantine

| Monitored | What it tells us | Action when it fails |
| --- | --- | --- |
| Residual mean on known-good periods | The model has developed a systematic bias. | Investigate; candidate for retraining. |
| Residual spread against the recorded error band | The model has become less precise than it was accepted at. | Widen confidence or retrain. |
| Operating-envelope coverage | The machine is now running outside what the model saw in training. | Residuals suppressed outside the envelope. |
| Input availability and validity | A required signal has degraded. | Dependent models marked unusable — see the dependency map. |
| Drift trend | Slow divergence caused by equipment, control or duty change. | Drift alert with lead time; scheduled retraining. |
| Post-repair behaviour | A machine that was repaired may have a legitimately new normal. | Re-baseline after verified major work. |

A model that fails its health standard is quarantined. Quarantine means its residuals stop being used for diagnosis — they are not merely flagged as weaker. Every fault class that depends on that residual returns NO_DIAGNOSIS until the model is restored, and the Copilot states which model is out of service and why.

## Model registry and versioning

| Field | Required |
| --- | --- |
| Model identity and version | Unique and immutable |
| Asset | The specific chiller, not the equipment class |
| Target signal | The one signal it predicts |
| Input list | Exact tags, with units |
| Training window and exclusions | Dates and reasons |
| Operating envelope | Load and temperature ranges covered |
| Accepted error band | The precision the model was approved at |
| Owner | A named reliability or data engineer |
| Status | Candidate / shadow / production / quarantined / retired |
| Rollback version | The last known-good version |
| Evaluation suite | The tests it must pass to be promoted |

The model version travels with every residual into the evidence pack, so any diagnosis in the platform can be traced back to the exact model that produced the numbers behind it — including months later, after the model has been retrained.

## Retraining

| Trigger | Handling |
| --- | --- |
| Drift detected | Scheduled retraining with engineer review |
| Equipment modified or overhauled | Re-baseline; the old normal no longer applies |
| Control strategy or setpoint regime changed | Re-baseline |
| Duty or seasonal envelope extended | Extend training coverage rather than replace the model |
| Instrumentation changed or recalibrated | Re-baseline any model using that tag |
| Verified major repair completed | Re-baseline once the machine has run steadily under the new condition |

### Retraining rules

A model is never retrained on a period containing a known unresolved fault — that teaches the model that the fault is normal.

A new version runs in shadow alongside the current one before promotion, and must beat it on the evaluation suite.

Promotion is an approved, recorded change with a named owner and a rollback version.

Retraining is never triggered automatically by a diagnosis being disputed.

## The trust contract between the layers

| Layer | Supplies | Must never supply |
| --- | --- | --- |
| Equipment ML | Predictions, residuals, validity flags, model version, envelope status | A fault name, a cause, or a recommendation |
| FDD rules | Gates, persistence, fault class, confidence, the rule path taken | A free-text explanation |
| Copilot / LLM | Explanation, comparison, drafts, next-step proposals | A fault class, a number it did not retrieve, or an authorisation |
| Control Plane | Allow, approve, deny, and the audit record | A diagnosis |

## What must stay deterministic

These components carry safety, money and legal consequence. None of them may be probabilistic, and none may be delegated to a model.

| Component | Why it must be deterministic |
| --- | --- |
| Operating gates | They decide whether any judgement is permitted at all. |
| Fault isolation path | It must produce the same class from the same residuals, every time, and be auditable line by line. |
| Persistence and volatility rules | They separate a fault from a passing disturbance. |
| Sensor-bias checks | They stop instrumentation faults being reported as equipment faults. |
| Priority calculation | The number drives crews, cost and SLA exposure, and must be explainable to a customer. |
| Work order state machine | Illegal transitions must be impossible, not merely unlikely. |
| Scope, RBAC and tenant isolation | One probabilistic mistake here is a data breach. |
| Approval routing | Who must approve what is a policy question, not a prediction. |
| Idempotency keys | A retry must never create a second work order. |
| SLA clocks and audit writes | They are evidence, and evidence cannot be approximate. |
| Safety interlocks and permits | Safety is never inferred. |

## ML layer service targets

| Measure | Target |
| --- | --- |
| Residual availability during valid running periods | 99% or better per asset |
| Models in production meeting their health standard | 100% — anything failing is quarantined, not tolerated |
| Diagnoses issued while a required model was quarantined | Zero |
| Gate correctness on the labelled test set | 100% — gates are rules, not predictions |
| Drift detection lead time before residuals become unusable | Measured and improving |
| Faults later attributed to instrumentation rather than equipment | Falling — tracked as a data-quality metric, not a diagnosis failure |
| Model version present in the evidence pack | 100% |

# 31. Low-Level Engineering Contracts

The architecture becomes production-grade when every workflow component has a precise contract.

## 31.1 Tool contract

| Field | Required |
| --- | --- |
| Tool identity/version | Unique immutable version |
| Owner | Engineering/service owner |
| Input schema | Strict validation |
| Output schema | Typed validation |
| Read/write | Explicit category |
| Allowed agents/roles | Allowlist |
| Tenant/asset scope | Required |
| Risk | LOW/MEDIUM/HIGH/etc. |
| Approval | Explicit rule |
| Idempotency | Required for writes |
| Timeout/retry | Bounded |
| Side effects | Documented |
| Audit | Mandatory for material actions |

## 31.2 Policy decision contract

Every action should resolve to:

POLICY RESULT ALLOW ¦ ALLOW-WITH-APPROVAL ¦ READ-ONLY ¦ ESCALATE ¦ DENY

Decision input: user + role + customer account + scope + intent + action + asset criticality + risk + safety + current state + rule version.

## 31.3 Evidence pack contract

| Evidence | Required information |
| --- | --- |
| Source | Telemetry/document/WO/system |
| Timestamp | Freshness |
| ML/FDD | Model/rule/version |
| Operating state | Gate result |
| Measurements | Residuals/values/trends |
| History | Similar verified cases |
| Knowledge | Source/version |
| Confidence | Known / likely / ambiguous |
| Decision | Why suggestion follows |

# 32. The AI Control Plane

This is the governed execution layer between users/Copilot and agents/tools/enterprise systems.

| Control domain | What it enforces |
| --- | --- |
| Identity & RBAC/ABAC | Who the user/agent is and what scope they possess |
| Tenant / asset scope | Which customer, site, equipment and data may be accessed |
| AI action rule | READ / ANALYZE / RECOMMEND / DRAFT / APPROVE / EXECUTE / VERIFY |
| Risk engine | LOW / MEDIUM / HIGH / SAFETY-CRITICAL / SYSTEM-CRITICAL |
| Approval engine | Who must approve which action and under what conditions |
| Safety / permit engine | SOP, permit, qualification, isolation/LOTO and EHS gates |
| Agent registry | Agent purpose, features, tools, boundaries and version |
| Tool gateway | Schema validation, authorization, credentials, safe retry without creating duplicates, side effects |
| Evidence / where the information came from | Source, timestamp, model/FDD/rule version, confidence and lineage |
| State / coordination | Durable workflow state, retries, timeouts, recovery |
| Audit | Immutable action and decision trail |
| Observability | Agent/tool/model/RAG/action/verification metrics |
| Governance | Model, prompt, FDD, rule and configuration lifecycle |
| Resilience | Backup, recovery, degraded mode and offline field behaviour |

# 33. Security, Safety and Threat Model

| Threat | Example | Primary control |
| --- | --- | --- |
| Prompt injection | Document tells agent to ignore rule | Instruction/data separation + tool rule |
| Broken access control | Cross-site/customer query | RBAC/ABAC + tool-side scope |
| Excessive agency | Agent closes critical WO | Risk + approval + state rule |
| Credential abuse | Agent receives raw CMMS password | Credential broker + short-lived scoped identity |
| Data leakage | Sensitive data in report/export | Classification + row/column/scope security |
| Tool abuse | Malformed dangerous parameters | Schema validation + allowlists |
| Data/model poisoning | Bad equipment readings/knowledge drives decision | Quality + where the information came from + quarantine |
| Resource exhaustion | Runaway agent loop | Rate/step/time/token budgets |
| Audit failure | Write without trace | Mandatory audit gate |
| Concurrency race | Two users update same WO | Versioning + optimistic locking + state checks |

## 33.1 Safety action matrix

| Action class | AI suggestion | AI execution | Human control |
| --- | --- | --- | --- |
| Routine low-risk | Yes | Policy may allow | Defined role |
| Maintenance with moderate risk | Yes | Approval/rule | Supervisor/manager as configured |
| Critical asset intervention | Yes with evidence | Approval required | Authorized approver |
| Safety-critical / LOTO | Controlled only | No autonomous authorization | EHS/allowed human |
| Control/configuration change | Highly restricted | Privileged change process | Explicit allowed human |

## 33.2 Break-glass

Emergency elevation must be temporary, explicitly allowed, scoped, fully audited and automatically expire. It must not become a permanent administrator bypass.

# 34. Data, RAG and Report Governance

## 34.1 Data product contract

| Field | Requirement |
| --- | --- |
| Owner | Named data owner |
| Schema | Versioned contract |
| Classification | Public/Internal/Operational/Sensitive/Critical as applicable |
| Freshness | Defined SLA |
| Quality | Defined validity/completeness rules |
| Lineage | Source → transformation → output |
| Retention | Defined rule |
| Tenant scope | Enforced |
| Consumer | Known services/agents/reports |

## 34.2 RAG rules

Retrieved content is data, not authority.

System rules and tool rules cannot be overridden by retrieved documents.

Retrieval is customer account/site/asset scoped.

Source/version/freshness are preserved.

Conflicting sources produce an explicit uncertainty state.

Unverified created by AI content is not automatically promoted to trusted knowledge.

## 34.3 Report lineage

REPORT → KPI → CALCULATION → SOURCE DATA → SOURCE RECORDS → TIMESTAMP / VERSION

EXECUTIVE TRUST RULE Every important number should be explainable: where it came from, how it was calculated, how fresh it is and what scope was used.

# 35. Priority Workflows

## 35.1 Report → Insight → Action

REPORT → USER QUESTION → COPILOT → AUTHORIZATION → ANALYSIS → EVIDENCE → RECOMMENDATION → WO / ESCALATION

## 35.2 Fault → Fix → Proof

ML/FDD → EVIDENCE → DIAGNOSIS → AI EXPLANATION → MAINTENANCE RECOMMENDATION → WO → TECHNICIAN → POST-WORK DATA → VERIFICATION → PASS/CLOSE or FAIL/REOPEN

## 35.3 Technician workflow

MY WORK → OPEN WO → AI EXPLAINS → SAFETY → SOP/CHECKLIST → PARTS → EXECUTE → FINDINGS → REPAIR → COMPLETE → VERIFY

## 35.4 Executive workflow

ASK → ENTERPRISE SCOPE → KPI REPORT → DRILL-DOWN → TOP RISKS → ACTIONS → OUTCOME / ROI

## 35.5 Unallowed workflow

REQUEST → IDENTITY/SCOPE → DENY → NO DATA / NO SIDE EFFECT → AUDIT → OPTIONAL ESCALATION

## 35.6 Bad-data workflow

DATA QUALITY FAIL → NO_DIAGNOSIS → EXPLAIN LIMITATION → INSTRUMENTATION/DATA-QUALITY ACTION → RECHECK

# 36. Feature → Agent → Control → Outcome Matrix

| Feature | Agent/service | Control | Evidence | Outcome |
| --- | --- | --- | --- | --- |
| Report generation | Reporting Agent | Scope + export rule | KPI lineage | Trusted report |
| Fault explanation | Reliability Agent | FDD/evidence grounding | Residuals + gates | Understand fault |
| WO creation | WO/Maintenance Agent | Action rule + approval | WO payload + audit | Controlled WO |
| WO assignment | Planning Agent | Skills + scope | Assignment decision | Qualified owner |
| Parts action | Inventory Agent | Financial/inventory rule | Stock/ETA | Ready-to-execute work |
| Technician guidance | Copilot + Knowledge | Safety + scope | SOP/source | Safe execution |
| Repair closure | Verification Agent | Verification rule | Post-work evidence | Verified repair |
| Customer export | Reporting service | Tenant + recipient rule | Export audit | Controlled delivery |

# 37. Validation, Testing and Production Acceptance

10/10 architecture requires proof, not only documentation.

| Test area | Example acceptance test |
| --- | --- |
| Authorization | Unallowed asset request returns DENY with zero data leakage |
| Tool security | Unallowed write cannot reach CMMS |
| Approval | Critical WO cannot execute without valid approval |
| Safety | Safety-critical action cannot bypass safety gate |
| Prompt injection | Malicious document cannot change rule/tool authority |
| RAG isolation | Cross-customer account retrieval is blocked |
| Data quality | Invalid operating state results in NO_DIAGNOSIS |
| Idempotency | Retry after timeout does not duplicate WO |
| Concurrency | Conflicting WO updates resolve safely |
| State machine | Invalid state transition is rejected |
| Evidence | Material suggestion exposes source/version/evidence |
| Verification | Failed repair verification reopens/escalates |
| Audit | Material action has complete trace |
| Recovery | Dependency outage results in defined safe/degraded mode state |
| Report accuracy | Reported KPI reconciles with source calculation |

## 37.1 Release gates

| Gate | Required evidence | Decision |
| --- | --- | --- |
| G0 Design | Use case, risk, threat model, owners | Proceed / redesign |
| G1 Data | Quality, lineage, privacy/security | Proceed / block |
| G2 AI | validation, grounding, red-team, evaluation | Approve / reject |
| G3 Action | Tool, rule, approval, safety tests | Approve / reject |
| G4 Production | service target, audit, rollback, incident plan | Go / no-go |
| G5 Post-release | Monitoring, incidents, drift, outcomes | Continue / remediate / rollback |

# 38. Observability, Service Targets and Operations

| Domain | Measure |
| --- | --- |
| Copilot | Latency, task success, escalation, grounded answer rate |
| Agents | Workflow success, failed trajectories, retries, step count |
| Tools | Latency, timeout, schema failure, side-effect success |
| RAG | Retrieval quality, stale-source rate, grounding failures |
| FDD | Diagnosis validity, false positives, NO_DIAGNOSIS correctness |
| WOs | SLA, cycle time, backlog, verification pass/reopen |
| Reports | Generation success, KPI reconciliation against source |
| Security | Unallowed-action block rate, incident MTTR |
| Control plane | Policy decision latency, approval latency, audit completeness |
| Business | Downtime avoided, MTTR, cost, energy, PM compliance |

## 38.1 Resilience

Define RTO/RPO for control plane, state, audit and integrations.

Back up and test restoration.

Provide read-only/degraded mode behavior when critical dependencies are unavailable.

Reconcile state before retrying uncertain external writes.

Support controlled offline field capture where required.

Have incident containment, rollback and credential/rule revocation procedures.

# 39. AI Governance, Change and Learning

| Artifact | Versioned? | Evaluation? | Audit? |
| --- | --- | --- | --- |
| Model | Yes | Yes | Yes |
| Agent | Yes | Yes | Yes |
| Prompt/instruction | Yes | Yes | Yes |
| Tool contract | Yes | Yes | Yes |
| FDD rule | Yes | Yes | Yes |
| Policy | Yes | Simulation + test | Yes |
| Approval matrix | Yes | Scenario tests | Yes |
| SOP/RAG source | Yes | Retrieval/grounding tests | Yes |
| Workflow/state machine | Yes | Transition tests | Yes |

## 39.1 Human override

When a human rejects or changes an AI suggestion, capture the reason, evidence and eventual outcome. Human override is a governed learning signal—not an automatic training label.

## 39.2 Policy simulation

Before deploying a rule change, replay representative historical requests in dry-run mode and compare ALLOW / APPROVAL / DENY outcomes with the current rule.

# 40. Global-Standard Alignment

The architecture is designed against recognized frameworks and practices. This is an alignment target, not a claim of certification.

| Framework / practice | Graylinx use |
| --- | --- |
| NIST AI RMF 1.0 | GOVERN → MAP → MEASURE → MANAGE; AI risk lifecycle |
| ISO/IEC 42001:2023 | AI management system, accountability and continual improvement |
| ISO/IEC 23894:2023 | AI-specific risk identification, treatment and monitoring |
| NIST CSF 2.0 | Cybersecurity governance, protection, detection, response and recovery |
| OWASP LLM / application security | Prompt injection, access control, insecure tool use, supply chain, logging and resource abuse |
| Zero Trust principles | Never trust by default; authenticate, authorize and continuously validate |
| Industrial safety practices | Safety-critical work requires controlled human authorization and fail-safe behavior |

## 40.1 Governance operating cycle

CONTINUOUS GOVERNANCE PLAN → RISK ASSESS → DESIGN → BUILD → TEST / validation → APPROVE → DEPLOY → MONITOR → REVIEW → IMPROVE

## 40.2 Non-negotiable global practices

Policy is enforced outside the LLM.

Tool/API boundaries enforce authorization independently.

Safety cannot be overridden by prompts.

Unknown/ambiguous is a valid outcome.

High-risk actions require explicit human control.

Persistent external changes are auditable.

Production AI components are versioned and evaluated.

Tenant boundaries are enforced independently at retrieval and execution.

# 41. Business Value and ROI

| Outcome | Measure |
| --- | --- |
| Availability | Asset uptime / availability improvement |
| Reliability | MTBF, repeat failure reduction |
| Maintenance | MTTR, PM compliance, backlog, SLA |
| Downtime | Hours avoided / reduced |
| Cost | Labor, parts, downtime and avoided cost |
| Energy | Energy anomaly reduction / savings |
| AI effectiveness | Recommendation acceptance, verification success |
| Operational trust | False positive rate, escalation rate, audit completeness |

NORTH-STAR BUSINESS LOOP INTELLIGENCE → DECISION → WORK ORDER → REPAIR → VERIFICATION → BUSINESS OUTCOME → ROI

# 42. Implementation Blueprint

## 42.1 Service boundaries

| Component | Owns | Must not own |
| --- | --- | --- |
| Copilot API | Conversation/session entry | Direct uncontrolled writes |
| Control Plane | Policy, identity/scope decisions, approval, audit | Business-specific diagnostic logic |
| Orchestrator | Workflow coordination/state | Policy bypass |
| Agent services | Domain reasoning/suggestion | Unrestricted enterprise writes |
| Tool Gateway | Validated external actions | Free-form agent access |
| ML/FDD services | Equipment intelligence/evidence | User authorization |
| RAG service | Scoped retrieval | Policy authority |
| WO service | WO state and transactions | LLM rule decisions |
| Reporting service | Metrics/report artifacts | Scope expansion |
| Verification service | Outcome verification | Unverified closure |

## 42.2 Minimum state domains

Conversation state

Agent task state

Approval state

WO state

Tool execution state

Verification state

Audit/event state

## 42.3 Transaction rule

Every external write must be treated as a transactionally significant event: validate → authorize → execute once → reconcile → audit → verify.

# 43. Gap Closure Checklist

The following items were identified in cross-functional critique and are now explicitly represented in the target architecture.

| Gap | 10/10 treatment |
| --- | --- |
| ROI | Business KPI/ROI model |
| Production context | Operational/production impact considered in prioritization |
| Technician UX | Dedicated technician job execution workflow |
| Evidence | Formal evidence-pack contract |
| Model/agent registry | Explicit registry fields and lifecycle |
| Security | Threat classes + controls + tool-side enforcement |
| Compliance | Control/evidence mapping approach |
| Safety | Safety action category matrix |
| Data | Data product contract + lineage |
| Capability matrix | Persona → feature → data → agent → tool → approval → outcome |
| State machine | WO, approval, agent, tool and verification states |
| Concurrency | Idempotency + optimistic locking/state checks |
| Report security | Scope, export and scheduled-job reauthorization |
| Prompt injection | Input/content threat controls |
| Credential security | Credential broker/scoped identity |
| Break-glass | Temporary, audited emergency elevation |
| Policy versioning | Versioned rules + simulation |
| Evaluation | validation + release gates |
| Resilience | RTO/RPO + degraded mode/offline modes |
| Observability | Agent/tool/model/RAG/action/business service targets |

# 44. Final Architecture Review

| Dimension | 10/10 target |
| --- | --- |
| Product strategy | Reports + Work Orders + Synex Copilot are explicit P0 priorities |
| AI foundation | Existing ML/FDD remains the trusted equipment intelligence layer |
| Agentic layer | Agents coordinate; they do not own authority |
| Control plane | Identity → Scope → Risk → Policy → Approval → Safety → Tools → Audit |
| Evidence | Every material conclusion/action can be traced |
| Execution | External writes are typed, scoped, idempotent and state-aware |
| Safety | High-risk and safety-critical actions remain under explicit human control |
| Governance | Lifecycle, validation, versioning, simulation and continuous improvement |
| Operations | Observability, service targets, resilience, incident response and recovery |
| Business | Every major AI workflow can connect to an day-to-day/financial outcome |

FINAL VERDICT The 10/10 target is not 'more AI'. It is a platform where powerful AI features operate inside a strong, testable and auditable control system. The customer sees three simple things—Reports, Work Orders and Copilot—while the complexity is handled underneath.

GRAYLINX — INTELLIGENCE → DECISION → ACTION → VERIFICATION → OUTCOME

# APPENDIX

Reference

The same capabilities described in the simplest possible English, for onboarding, training and customer conversations.

# Appendix A — Plain-English Feature Guide

This section explains the main Graylinx features in simple English. For every feature, the goal is: what it does, who uses it, a real example, and what happens next.

## A. Reports — “Tell me what is happening.”

Who uses it: Executives, Plant Managers, Maintenance Managers, Reliability Engineers, Customers and other allowed users.

See the health of the company, plant, site, system or equipment.

See open, overdue and critical work orders.

See failures, repeat problems, downtime, energy use and maintenance cost.

Ask the Copilot to explain a report in simple words.

Move from a company-level number down to a site, equipment and sensor.

Example: A Plant Manager asks, “Which equipment needs attention today?”

What happens: Graylinx checks the manager’s allowed sites → checks equipment health and faults → ranks the important equipment → shows why each one needs attention → offers the next action.

Result: The manager does not need to search five dashboards manually.

## B. Work Orders — “Get the work done.”

Who uses it: Maintenance Managers, Supervisors, Planners, Technicians, Service Teams and allowed customers.

Create a work order manually or ask the Copilot to prepare one.

Set priority.

Get approval when needed.

Plan the time, technician and parts.

Record what the technician found and fixed.

Check whether the repair actually solved the problem.

Example: “Create a work order for Chiller-03 because the condenser performance is abnormal.”

What happens: Graylinx checks the equipment and supporting data → prepares the WO → checks the user’s permission and risk → asks for approval if required → creates the WO → assigns/plans it → tracks the work → checks the equipment after repair.

Important: A technician marking a WO complete does not automatically mean the problem is fixed.

## C. Synex Copilot — “Ask Graylinx.”

The Copilot is the simple front door. Behind it, the AI can use reports, equipment data, FDD, documents, work orders and approved tools.

| User says | Graylinx does | Example result |
| --- | --- | --- |
| “What is wrong with Chiller-03?” | Checks asset data, current readings, FDD and past work. | “The main issue is likely condenser performance. Here is the supporting data.” |
| “Why is it unhealthy?” | Explains the important readings and trends. | Simple explanation + proof. |
| “What should we do?” | Suggests the next inspection or maintenance step. | Recommended action with supporting data. |
| “Create a WO.” | Checks permission and risk, then drafts/creates through the controlled WO service. | WO draft or approval request. |
| “Show my overdue WOs.” | Uses the user’s allowed sites/assets and filters the data. | Clean overdue list. |
| “Did the repair work?” | Checks post-repair equipment readings and FDD. | PASS, FAIL or not enough information. |
| “Send this report to the customer.” | Checks whether the user can share it and whether the receiver is allowed. | Send, or safely refuse. |

## D. Asset View — “Show me everything about this equipment.”

Example: Open Chiller-03.

See where it belongs: customer → site → plant → system → equipment → component.

See current health and risk.

See past failures and work orders.

See important readings and trends.

See related equipment.

Ask the Copilot questions about the asset.

Example question: “Has this chiller had this problem before?”

Result: Graylinx searches the allowed history and shows similar past cases.

## E. FDD — “Find and explain problems.”

Graylinx already has ML models. The AI layer uses those results; it does not replace the equipment intelligence.

ML checks whether readings are different from normal.

FDD checks that the equipment is really in a valid operating state.

The system checks whether the problem lasts long enough to matter.

It checks whether the problem is getting worse or unstable.

If there is not enough proof, it can say: “I do not have enough information to diagnose this.”

Example: A pressure reading changes for 20 seconds and then returns to normal.

Result: Graylinx should not immediately create a critical fault. It waits for the defined checks and avoids a false alarm.

## F. Knowledge / Documents — “Tell me how to fix it.”

The Copilot can search allowed manuals, SOPs, previous work orders, verified cases and site documents.

Example: Technician asks, “What is the inspection procedure for this fault?”

Result: Graylinx finds the correct procedure, shows the source, and gives the technician the relevant steps.

Documents are supporting information, not permission to perform an unsafe action.

A document cannot override safety rules or system rules.

The user should be able to see where important information came from.

## G. Maintenance Planning — “What should we do first?”

Example: There are 20 open WOs and only two technicians available.

Graylinx considers equipment importance, fault risk, production impact, SLA, technician skill, parts and available maintenance time.

Result: It gives the planner a ranked list. The planner remains in control of the final decision when required.

## H. Inventory and Parts — “Do we have what we need?”

Example: A WO needs a compressor part.

Check whether the part is in stock.

Check whether another WO is already using it.

Check expected delivery.

Suggest reservation or purchase when allowed.

Tell the planner if the part will delay the job.

Result: Maintenance does not discover the missing part only after the technician arrives.

## I. Alerts — “Tell the right person at the right time.”

Examples:

Critical equipment fault → maintenance/reliability alert.

WO close to SLA breach → manager alert.

Safety issue → controlled safety escalation.

Bad sensor data → do not give a confident diagnosis; send a data-quality alert.

The system should avoid sending the same alert repeatedly. It should group related events and show the reason for the alert.

## J. Verification — “Did it really work?”

Example: A technician repairs Chiller-03 and marks the WO complete.

Graylinx checks the equipment again. If the readings return to the expected range and the fault clears, the result can be PASS. If the fault remains, the WO can be reopened or escalated.

This closes the loop: Detect → Work → Repair → Check → Prove.

## K. Safety — “AI must know when to stop.”

Example: A user asks the Copilot to perform a safety-critical change.

The Copilot does not simply follow the instruction. The Control Plane checks the action, risk, permission, required permit and human approval. If the action is not allowed, it is blocked and recorded.

Simple rule: AI can help people understand and prepare work. It must not bypass safety controls.

## L. Customer Assistance — “Give each customer only their own view.”

Example: Customer A asks for all equipment reports.

Graylinx checks Customer A’s account and allowed sites before retrieving anything. Customer A cannot use the Copilot to see Customer B’s data.

The same rule applies to reports, documents, work orders, equipment and AI actions.

## M. Executive Assistance — “Give me the answer, not 20 screens.”

Example: CEO asks, “How are we doing this month?”

The Copilot gives a short business summary, then offers drill-down into availability, downtime, maintenance cost, major risks and problem assets.

The executive can then ask: “Why did downtime increase?” and continue the investigation through the same conversation.

## N. Technician Assistance — “Help me do today's work.”

Example: Technician opens the WO for Chiller-03.

See the fault in simple language.

See safety requirements.

See the correct procedure.

See important past repair history.

See required parts.

Record findings through the Copilot.

Ask questions while working.

Finish the WO and start verification.

The technician should not need to understand which AI agent is running in the background.

## O. Complete Example — From Fault to Business Result

1. ML/FDD notices abnormal condenser behavior.
2. The system confirms the equipment is running in a valid state and the problem persists.
3. Reliability AI explains the finding using supporting data.
4. Maintenance AI suggests an inspection.
5. The manager asks the Copilot to create a WO.
6. The Control Plane checks permission and risk.
7. The WO is approved, planned and assigned.
8. The technician follows the procedure and records findings.
9. The repair is completed.
10. Graylinx checks the equipment after the repair.
11. If the fault clears, the WO is verified and closed.
12. The result appears in reports and becomes part of the maintenance history.

## P. Simple Rule for Every Feature

Every feature in Graylinx should make one of these four questions easier to answer:

1. What is happening?
2. Why is it happening?
3. What should we do?
4. Did it work?