G R A Y L I N X

Graylinx Synex — Feature Review Pack

Intelligent Operations, Connected by AI. Every feature on the platform, in one place, for product and SME review.

# 1. How to Use This Pack

This is a working document, not a reference document. Every feature and every open question carries an ID. Mark each row, then record what was agreed in the decision log at the end. The full detail behind any row is in the main document — this pack exists so that a review meeting can cover the whole platform without reading seventy-eight pages.

| Mark | Meaning | What happens next |
| --- | --- | --- |
| A | Agreed as written | No action — goes into the build backlog as specified |
| C | Change requested | Note the change in the decision log; the main document is updated |
| Q | Question / needs data | Owner and due date recorded; blocks the feature until answered |
| D | Defer | Moves to a later phase; recorded with the reason |
| X | Out of scope | Removed from the feature register with a reason |

Engine column: SW = plain deterministic software · R = deterministic rule · ML = equipment machine-learning model · LLM = language model / agentic layer. Anything marked R or SW must produce the same answer every time from the same inputs, and is testable line by line.

# 2. The Platform on One Page

ASK → UNDERSTAND → FIND DATA → EXPLAIN → RECOMMEND → CREATE / ACT → VERIFY → REPORT → LEARN

| Layer | What sits here | Engine | Who owns it |
| --- | --- | --- | --- |
| Data and digital twin | BMS acquisition, tag normalisation, hierarchy, quality flags | SW | Data / IoT |
| Equipment ML | Six normal-operation models per chiller; residuals and validity flags | ML | Reliability + Data |
| FDD and reliability | Operating gates, persistence, isolation path, fault class, confidence | R | Reliability + SME |
| Knowledge | SOPs, manuals, WO history, verified cases — retrieved with sources | LLM + retrieval | Maintenance |
| Synex Copilot | Understanding, explanation, planning, drafting, summarising | LLM | Product + AI |
| Control Plane | Identity, scope, risk, approval, tool gateway, audit | SW | Platform + Security |
| Execution | Work orders, planning, inventory, notifications, reports | SW | Maintenance + Platform |

| Priority | Pillar | One-line promise | Feature count in this pack |
| --- | --- | --- | --- |
| P0 | Synex Copilot | One assistant that understands, explains, prepares work and proves the result. | 14 |
| P0 | Reports | Ask a question, get the answer with the numbers behind it. | 10 |
| P0 | Work Orders | Work that arrives carrying its own justification and cannot close unproven. | 12 |
| P0 | Reliability / FDD | Find the fault, name one cause, or say honestly that we cannot. | 14 |
| P0 | Control Plane | Nothing acts without identity, scope, approval and an audit record. | 8 |
| P1 | Asset, Knowledge, Planning, Inventory, Alerts, Verification, Roles, Safety | Everything the loop needs to close. | 43 |

# 3. Feature Register

101 features across thirteen domains. This is the complete scope of the new AI layer — if something is not on this list, it is not being built.

## 3.1 Synex Copilot

| ID | Feature | What it does | Primary user | Engine | Pri | Mark |
| --- | --- | --- | --- | --- | --- | --- |
| C1 | Natural-language ask across the platform | One entry point to reports, assets, faults, work orders and documents. | Everyone | LLM + SW | P0 |  |
| C2 | Context resolution | Understands “this” and “it” from the screen and the conversation. | Everyone | LLM + SW | P0 |  |
| C3 | Intent routing | Chooses the right skill and tools for the request. | Everyone | LLM | P0 |  |
| C4 | Evidence pack assembly | Collects the readings, versions and records behind every answer. | Everyone | SW | P0 |  |
| C5 | Grounded fault explanation | Explains the FDD rule path in plain English, without inventing it. | Reliability | LLM | P0 |  |
| C6 | Ranked recommendation | Proposes next actions with reason, confidence and alternatives. | Maintenance | LLM + R | P0 |  |
| C7 | Honest uncertainty | Returns NO_DIAGNOSIS when gates fail or signals conflict. | Everyone | R | P0 |  |
| C8 | Draft before write | Shows the complete action before anything is saved. | Everyone | SW | P0 |  |
| C9 | Approval request routing | Prepares the request and names the approver; never self-approves. | Supervisor | SW | P0 |  |
| C10 | Multi-step task memory | Carries a job from investigation to work order to verification. | Everyone | SW | P0 |  |
| C11 | Role-scoped answers | Same assistant, different scope and depth per role. | Everyone | SW | P0 |  |
| C12 | Source-cited knowledge answers | Quotes the SOP or manual and shows where it came from. | Technician | LLM | P0 |  |
| C13 | Watches | “Tell me if this gets worse” — a monitored condition with a notification. | Plant Manager | R | P1 |  |
| C14 | Executive briefing | Condenses the week into a short business summary with drill-down. | Executive | LLM | P1 |  |

## 3.2 Reports

| ID | Feature | What it does | Primary user | Engine | Pri | Mark |
| --- | --- | --- | --- | --- | --- | --- |
| R1 | Ask a question of a report | Conversational follow-up on any report. | All | LLM | P0 |  |
| R2 | Create report from natural language | Builds a report from a spoken or typed request. | Manager | LLM + SW | P0 |  |
| R3 | Explain a KPI change | Traces a movement to the equipment, faults and work behind it. | Manager | LLM + SW | P0 |  |
| R4 | Compare sites, assets or periods | Aligns two scopes on identical metric definitions. | Regional Head | SW | P0 |  |
| R5 | Drill down to source records | Every number opens to the records that produced it. | Analyst | SW | P0 |  |
| R6 | AI narrative | Writes the commentary over verified metrics only. | Executive | LLM | P1 |  |
| R7 | Schedule and deliver | Recurring role-aware delivery. | Manager | SW | P1 |  |
| R8 | Export with lineage | Export carries metric definitions and source references. | Analyst | SW | P1 |  |
| R9 | Customer-scoped report | Customers see only their own sites and assets. | Customer | SW | P0 |  |
| R10 | KPI reconciliation | Reported numbers are checked against the source calculation. | Finance | SW | P0 |  |

## 3.3 Work Orders

| ID | Feature | What it does | Primary user | Engine | Pri | Mark |
| --- | --- | --- | --- | --- | --- | --- |
| W1 | Create work order from chat | From a sentence, with the evidence attached. | Maintenance | LLM + SW | P0 |  |
| W2 | Create work order from a fault | Direct from an FDD finding, pre-populated. | Reliability | R + SW | P0 |  |
| W3 | Evidence auto-attached | Residuals, gates, trends and similar cases travel with the job. | Technician | SW | P0 |  |
| W4 | Priority calculation | Deterministic formula over criticality, risk, SLA and production impact. | Planner | R | P0 |  |
| W5 | Maintenance window planning | Finds a production-compatible slot. | Planner | SW | P1 |  |
| W6 | Technician assignment | Matches skills, certifications and availability. | Supervisor | SW | P1 |  |
| W7 | Parts check and reservation | Stock, alternates, delivery impact. | Stores | SW | P1 |  |
| W8 | Findings capture | Structured technician findings, readings and photographs. | Technician | SW | P0 |  |
| W9 | Verification gate before close | A work order cannot close unproven. | Supervisor | R | P0 |  |
| W10 | Reopen on failed repair | Previous findings preserved for the next technician. | Supervisor | SW | P0 |  |
| W11 | Closure summary | What was found, what was done, what it proved. | Manager | LLM | P1 |  |
| W12 | SLA escalation | Routes when work approaches or breaches its SLA. | Manager | R | P1 |  |

## 3.4 Asset Intelligence

| ID | Feature | What it does | Primary user | Engine | Pri | Mark |
| --- | --- | --- | --- | --- | --- | --- |
| A1 | One equipment story | Health, status, faults, history, documents and risks in one view. | All | SW + LLM | P1 |  |
| A2 | Health score with reasons | Not just a number — the contributing factors. | Reliability | R + ML | P1 |  |
| A3 | Dependency and served load | What this machine feeds and what feeds it. | Operations | SW | P1 |  |
| A4 | Like-for-like comparison | Compares similar machines under similar conditions only. | Reliability | SW | P1 |  |
| A5 | Repeat-failure / bad-actor detection | Surfaces the assets consuming disproportionate effort. | Reliability | R | P1 |  |

## 3.5 Reliability and Fault Detection — primary SME review area

| ID | Feature | What it does | Primary user | Engine | Pri | Mark |
| --- | --- | --- | --- | --- | --- | --- |
| F1 | Six normal-operation models per chiller | DP, SP, DT, Power, Compressor Amps, Condenser Leaving. | Reliability | ML | P0 |  |
| F2 | Residual computation | Actual minus predicted, with a validity flag per residual. | Reliability | ML | P0 |  |
| F3 | Operating gates | Running steady, load above floor, flows valid, no setpoint change. | Reliability | R | P0 |  |
| F4 | Persistence and volatility test | Separates a fault from a passing disturbance. | Reliability | R | P0 |  |
| F5 | Deterministic isolation path | Power → head → water side vs refrigerant side → single class. | Reliability | R | P0 |  |
| F6 | Sensor bias / model mismatch detection | Rules out instrumentation before dispatching a crew. | Reliability | R | P0 |  |
| F7 | Honest ambiguity labels | High head — ambiguous; undercharge and restriction kept combined. | Reliability | R | P0 |  |
| F8 | NO_DIAGNOSIS on failed gates | No softened guess when the inputs are not trustworthy. | Reliability | R | P0 |  |
| F9 | Similar verified case matching | Finds past cases with the same signature and a proven fix. | Maintenance | SW | P1 |  |
| F10 | Model health and drift monitoring | Detects a model going quietly stale. | Data / Reliability | ML + R | P0 |  |
| F11 | Model quarantine | A failed model stops being used, not merely flagged. | Data / Reliability | SW | P0 |  |
| F12 | Re-baseline after verified major work | A repaired machine may have a legitimately new normal. | Reliability | ML | P1 |  |
| F13 | Cooling tower assessment | Wet bulb, approach and tower running hours. | Reliability | ML + R | P1 |  |
| F14 | Chilled-water ΔT health check | Flags sustained low ΔT against the design band. | Reliability | R | P0 |  |

## 3.6 Knowledge

| ID | Feature | What it does | Primary user | Engine | Pri | Mark |
| --- | --- | --- | --- | --- | --- | --- |
| K1 | SOP search | Approved procedures, retrieved with the source shown. | Technician | LLM | P1 |  |
| K2 | Manufacturer manual search | What the OEM actually says about this model. | Technician | LLM | P1 |  |
| K3 | Work order history search | “How was this fixed last time?” | Maintenance | LLM | P1 |  |
| K4 | Verified case search | Only fixes that were proven to work. | Reliability | LLM | P1 |  |
| K5 | Source-visible answers | Every important answer names its document and version. | All | SW | P0 |  |
| K6 | Explain a technical document simply | Turns dense OEM text into plain English. | Technician | LLM | P2 |  |

## 3.7 Planning and Inventory

| ID | Feature | What it does | Primary user | Engine | Pri | Mark |
| --- | --- | --- | --- | --- | --- | --- |
| PL1 | Prioritised work queue | Ranked by risk, criticality, SLA and production impact. | Planner | R | P1 |  |
| PL2 | Maintenance window finder | Slots that production can actually give. | Planner | SW | P1 |  |
| PL3 | Certification-aware matching | Only people qualified for the task. | Supervisor | SW | P1 |  |
| PL4 | Workload balance | Avoids overloading one crew. | Supervisor | SW | P2 |  |
| PL5 | Plan feasibility answer | “Can we actually do this tomorrow?” in one turn. | Planner | SW + LLM | P1 |  |
| I1 | Stock check | Availability and location. | Stores | SW | P1 |  |
| I2 | Reservation against a work order | Parts held for the job. | Stores | SW | P1 |  |
| I3 | Alternates | Acceptable substitutes when the primary part is out. | Stores | SW | P2 |  |
| I4 | Delivery impact on schedule | What the lead time does to the plan. | Planner | SW | P2 |  |

## 3.8 Alerts and Verification

| ID | Feature | What it does | Primary user | Engine | Pri | Mark |
| --- | --- | --- | --- | --- | --- | --- |
| L1 | Duplicate grouping | Forty alerts become one problem. | Operations | R | P1 |  |
| L2 | Alert explanation | Why this fired, in plain English. | Operations | LLM | P1 |  |
| L3 | Prioritisation | Ranked, not listed. | Operations | R | P1 |  |
| L4 | Routing | To the person who can act on it. | Operations | SW | P1 |  |
| L5 | Escalation | When it is not picked up or crosses a threshold. | Manager | R | P1 |  |
| L6 | Noise measurement | Alert volume tracked as a product metric. | Product | SW | P2 |  |
| V1 | Post-work residual comparison | Are the residuals back inside the band? | Reliability | ML + R | P0 |  |
| V2 | Valid comparison window | Comparison only under comparable operating conditions. | Reliability | R | P0 |  |
| V3 | Persistence across load range | Improvement must hold, not appear once. | Reliability | R | P0 |  |
| V4 | Fault-clear check | Does the FDD fault clear under valid conditions? | Reliability | R | P0 |  |
| V5 | Business outcome check | Did the expected energy or downtime improvement appear? | Manager | SW | P1 |  |
| V6 | PASS / FAIL / UNKNOWN | Three outcomes — UNKNOWN is a real and common answer. | Supervisor | R | P0 |  |
| V7 | Verified-case memory | Signature, fix and proven outcome written back for reuse. | Reliability | SW | P1 |  |

## 3.9 Roles, Safety and Control Plane

| ID | Feature | What it does | Primary user | Engine | Pri | Mark |
| --- | --- | --- | --- | --- | --- | --- |
| U1 | Customer view | Only their own sites, assets and reports. | Customer | SW | P0 |  |
| U2 | Executive brief | The answer, not twenty screens. | Executive | LLM | P1 |  |
| U3 | Technician job pack | Job context, safety, SOP, history, parts, findings. | Technician | LLM + SW | P0 |  |
| U4 | Planner queue view | What can be done, when, by whom. | Planner | SW | P1 |  |
| U5 | Permission explanation | “Why can’t this user see this report?” | Administrator | SW | P2 |  |
| S1 | Safety-critical action block | The AI stops; it does not weigh the risk itself. | EHS | SW | P0 |  |
| S2 | Permit and isolation gate | Permit, LOTO and isolation checks before work. | EHS | SW | P0 |  |
| S3 | Qualification check | Only qualified people are proposed for restricted work. | Supervisor | SW | P0 |  |
| S4 | Safety answers from the SOP | Never answered from model memory. | Technician | LLM | P0 |  |
| S5 | EHS escalation | Routed per the escalation matrix. | EHS | R | P0 |  |
| G1 | Identity and scope per turn | Scope recomputed every turn, never inherited. | Platform | SW | P0 |  |
| G2 | Risk classification | Low / medium / high / safety-critical / system-critical. | Platform | R | P0 |  |
| G3 | Approval engine | Who must approve what, under which conditions. | Platform | SW | P0 |  |
| G4 | Tool gateway | Schema validation, credentials, safe retry, side-effect control. | Platform | SW | P0 |  |
| G5 | Idempotency | A retry can never create a second work order. | Platform | SW | P0 |  |
| G6 | Audit trail | Every material action and decision, permanently. | Audit | SW | P0 |  |
| G7 | Break-glass | Emergency elevation that is temporary, recorded and expiring. | Security | SW | P1 |  |
| G8 | Policy versioning and simulation | Test a rule change before it goes live. | Governance | SW | P1 |  |

# 4. The Synex Copilot at a Glance

| Mode | Trigger | Writes? | Mode | Trigger | Writes? |
| --- | --- | --- | --- | --- | --- |
| ASK | A direct question of fact | No | APPROVE | A named human must agree | No |
| EXPLAIN | Why is this happening? | No | EXECUTE | Confirmed action | Yes |
| INVESTIGATE | Multi-step enquiry | No | VERIFY | Did the repair work? | Result |
| COMPARE | Two scopes or periods | No | ESCALATE | Safety or rule-driven routing | Yes |
| SEARCH | Documents and history | No | MONITOR | Tell me if it gets worse | Config |
| RECOMMEND | What should we do? | No | SUMMARIZE | Brief me | No |
| REPORT | Generate a report | Artifact | DRAFT | Prepare an action | No |

### Every turn ends in exactly one of six states

| ANSWERED | PARTIAL | NO_DIAGNOSIS | NEEDS_APPROVAL | BLOCKED | FAILED |
| --- | --- | --- | --- | --- | --- |
| Evidence sufficient and grounded. | Part answerable; the rest stated as missing. | Gates failed or signals conflict — with the data-quality action. | Permitted, but a named human must agree. | Scope, permission or safety prevents it. | A tool failed — with what was and was not done. |

THE ONE LINE THAT MATTERS The language model never names a fault and never grants a permission. The FDD rules name the fault; the Control Plane grants the permission. The Copilot explains both.

# 5. FDD Engine — For SME Review

## 5.1 The six models and their inputs

| Model | Predicts | Inputs | Residual | Mark |
| --- | --- | --- | --- | --- |
| DP | Discharge pressure | Suction pressure; cooling load; condenser water entry temp; condenser flow; lead/lag | rDP |  |
| SP | Suction pressure | Evaporator leaving; evaporator entry; evaporator flow / DPT; lead/lag | rSP |  |
| DT | Discharge temperature | Suction pressure; discharge pressure; cooling load; condenser water entry temp; condenser flow; lead/lag | rDT |  |
| Power | Chiller amps / power | Evaporator leaving temp; chiller load; condenser water entry temp; condenser flow | rPwr |  |
| Comp Amps | Compressor amps | Suction pressure; discharge pressure; chiller load; lead/lag | rAmp |  |
| Cond Leaving | Condenser water leaving temp | Chiller load; condenser water entry temp; condenser flow; lead/lag | rCWL |  |

## 5.2 Gates — nothing is diagnosed until all pass

| Gate | Proposed setting | Confirm with SME |
| --- | --- | --- |
| Running steady | No start, stop or stage transient in the window | Settling time after a stage change? |
| Load above minimum | Above the model’s valid load floor | What percentage load is the floor? |
| Flows valid | Evaporator and condenser flow signals healthy | Is condenser flow actually measured on site? |
| No setpoint change | No leaving-water setpoint move in the window | How long after a setpoint move before we trust residuals? |
| Persistence | Pattern held 20–30 minutes | Same window for every fault class, or per class? |

## 5.3 Fault fingerprints — the isolation path

| Fault class | rPwr | rDP | rCWL | rSP | rAmp | Separator | Mark |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Condenser water-side — low flow | High | High | High | — | — | Spiky / intermittent |  |
| Condenser water-side — fouling | High | High | High | — | — | Steady drift over weeks |  |
| Refrigerant-side high head | High | High | Normal | — | — | Water loop looks normal |  |
| High head — ambiguous | High | High | Noisy | — | — | Needs operator confirmation |  |
| Compressor inefficiency | High | Normal | — | Normal | High | Current high for the pressures |  |
| Starved evaporator | High | Normal | — | Low | — | Suction below expected |  |
| Expansion valve hunting | High | Normal | — | Oscillating | — | rSP and rDT swing repeatedly |  |
| Persistent starvation | High | Normal | — | Low, steady | — | Undercharge and restriction kept combined |  |
| DP sensor bias / model mismatch | Normal | High | Normal | — | Normal | Everything else normal |  |
| DT sensor bias | Normal | Normal | — | — | Normal | Only rDT abnormal |  |
| No diagnosis | any | any | any | any | any | A gate failed or signals conflict |  |

rDT is a support signal only. It is not used to separate the high-head causes.

## 5.4 What happens when a signal is missing

| Missing signal | Models lost | Diagnostic capability lost | Platform behaviour |
| --- | --- | --- | --- |
| Condenser flow | DP, DT, Power, Cond Leaving — four of six | The whole efficiency and high-head branch. Condenser water-side, refrigerant-side and compressor inefficiency can no longer be separated. | NO_DIAGNOSIS + data-quality work order |
| Evaporator flow / DPT | SP | Starved evaporator and valve hunting. | NO_DIAGNOSIS for evaporator-side classes |
| Chiller power | Power | The symptom that starts the isolation path. | No efficiency fault can be raised |
| Compressor lead/lag | DP, SP, DT, Comp Amps, Cond Leaving | Residuals shift at every stage change. | Gate fails on transitions |
| Condenser water entry temp | DP, DT, Power, Cond Leaving | Head behaviour cannot be normalised for water conditions. | NO_DIAGNOSIS for condenser-side classes |

# 6. Data and Instrumentation Requirements

The column on the right is for the site survey. A feature cannot be committed to a site until its required signals are confirmed available and trustworthy.

| Signal | Required for | Criticality | Available on site? |
| --- | --- | --- | --- |
| Suction pressure | DP, SP, DT, Comp Amps | Essential |  |
| Discharge pressure | DP, DT, Comp Amps | Essential |  |
| Discharge temperature | DT | Essential |  |
| Compressor amps | Comp Amps | Essential |  |
| Chiller power (external meter preferred) | Power — the start of the isolation path | Essential |  |
| Evaporator entering water temperature | SP; evaporator ΔT | Essential |  |
| Evaporator leaving water temperature | SP, Power; evaporator ΔT | Essential |  |
| Condenser entering water temperature | DP, DT, Power, Cond Leaving; condenser ΔT | Essential |  |
| Condenser leaving water temperature | Cond Leaving; condenser ΔT | Essential |  |
| Condenser flow | DP, DT, Power, Cond Leaving; efficiency proxy | Highest leverage single measurement |  |
| Evaporator flow / DPT | SP; efficiency proxy | High |  |
| Compressor lead/lag state | Five of six models | High |  |
| Wet bulb temperature | Cooling tower assessment | Medium |  |
| Outside air temperature | Air-cooled equivalents | Medium |  |

# 7. What Is ML, What Is Rules, What Is the LLM

| Question | Decided by | Never decided by |
| --- | --- | --- |
| Is this reading abnormal, and by how much? | The ML model, as a residual | Rules or the LLM |
| Is the equipment fit to be judged at all? | A deterministic gate | ML or the LLM |
| Has the pattern lasted long enough? | A deterministic persistence rule | The LLM |
| Which fault class is this? | The deterministic isolation path over the residuals | The LLM |
| How confident should we be? | Gate results plus the rule path | The LLM’s tone |
| What does it mean in plain English? | The LLM | — |
| What should we do about it? | LLM proposes, rules rank, a human decides | The LLM alone |
| What priority does the work get? | A deterministic formula | The LLM |
| Is this person allowed to do this? | Plain software — the Control Plane | ML or the LLM |
| Did the repair actually work? | Post-work residuals judged by a deterministic rule | The closure note or the LLM |

# 8. Open Questions for SME Sign-Off

These are the decisions that block build work. Each needs a value, a range or a yes/no from the SME. Proposed values are starting points for discussion, not commitments.

| ID | Question | Why it blocks | Proposed starting point | Decision |
| --- | --- | --- | --- | --- |
| Q1 | Is condenser flow measured at the target sites, and is the signal trustworthy? | Four of six models depend on it. Without it, most of the fault classes cannot be separated. | Meter it; otherwise scope the site to evaporator-side and sensor-fault classes only |  |
| Q2 | How is evaporator flow derived — measured, from DPT, or assumed constant? | Determines whether rSP is trustworthy and whether the efficiency proxy is meaningful. | Confirm provenance per site before any rSP-based class is enabled |  |
| Q3 | What is the minimum load for a valid diagnosis? | Below it the models are outside their trained envelope. | Confirm per machine type |  |
| Q4 | How long after a start or stage change before residuals are trusted? | Transients produce false abnormalities. | To be set with SME |  |
| Q5 | How long after a leaving-water setpoint change? | Same reason. | To be set with SME |  |
| Q6 | Persistence window — one value or per fault class? | Too short creates noise; too long delays real faults. | 20–30 minutes as a common default |  |
| Q7 | Healthy chilled-water ΔT band per machine. | Drives the ΔT health check and a common early warning. | Design ΔT from the machine data sheet; sustained deviation flagged |  |
| Q8 | Condenser approach temperature thresholds for fouling. | Separates fouling severity levels. | Per OEM data sheet, confirmed with SME |  |
| Q9 | Time constants that separate low condenser flow from fouling. | Both raise rDP and rCWL; only the shape differs. | Low flow = spiky/intermittent; fouling = steady drift over weeks |  |
| Q10 | Refrigerant-side high head — split overcharge from non-condensables, or keep combined? | Affects the corrective action given to the technician. | Keep combined until instrumentation supports a split |  |
| Q11 | Starved evaporator — confirm undercharge and restriction stay combined. | The available sensors cannot separate them. | Keep combined and label the ambiguity honestly |  |
| Q12 | Volatility threshold that defines expansion valve hunting. | Distinguishes hunting from steady starvation. | To be set from observed data with SME |  |
| Q13 | Sensor drift thresholds per sensor type before declaring sensor bias. | Stops instrument faults being reported as equipment faults. | Per sensor class, confirmed with SME |  |
| Q14 | Is compressor lead/lag state reliably available from the BMS? | Five of six models use it. | Confirm per site during survey |  |
| Q15 | What proves a condenser cleaning worked? | Defines the verification PASS criteria. | rPwr, rDP and rCWL back inside band, held several days across a representative load range |  |
| Q16 | Re-baseline policy after an overhaul — who authorises, and how long must the machine run first? | A repaired machine has a new normal; baselining too early locks in a transient. | SME authorises; minimum steady running period to be agreed |  |
| Q17 | Is the cooling tower in scope for phase one? | Tower condition drives condenser water behaviour and can mimic chiller faults. | Recommend in scope for assessment, out of scope for control |  |
| Q18 | Relative weighting of criticality, SLA and production impact in the priority formula. | Determines what crews do first. | Draft weighting to be reviewed with operations |  |
| Q19 | Which actions require SME sign-off rather than supervisor approval? | Sets the approval matrix for refrigerant-circuit work. | Refrigerant-circuit work proposed as SME sign-off |  |
| Q20 | Are there fault classes missing from section 5.3? | The register is the committed scope. | Open — SME to add |  |

# 9. Decision Log

Filled in during and after the review session. Anything recorded here is what gets built — the main document is updated from this log.

| ID | Mark | Decision agreed | Owner | Date | Reflected in main doc? |
| --- | --- | --- | --- | --- | --- |