Sensors Available:

Suction Pressure, Discharge Pressure, Discharge temperature, Compressor Amps, Evaporator In and Out, Condenser In and Out (for Water Cooled Chillers), Outside Air Temperature (Air Cooled), Wet Bulb Temperature (for Water Cooled Chillers), DPT/Flow meter (Only for Primary variable chillers), external energy meter for chillers in some cases

Computed parameter:

Evaporator delta t = evaporator in – evaporator out

Condenser delta t = condenser out – condenser in

Efficiency Proxy = (Condenser delta t *Condensor Flow)/ (Evaporator delta t*Evaporator Flow)

Models

Model DP – Discharge Pressure

DP = f(Suction Pressure, Chiller Cooling Load, Condenser Water Entry Temp, Condensor Flow, Compressor Lead/Lag)

Model SP – Suction Pressure

SP = f(Evaporator Leaving, Evaporator Entry, Evaporator Flow/DPT, Compressor Lead/Lag)

Model DT – Discharge Temperature

DT = f(Suction Pressure, Discharge Pressure, Chiller Cooling Load, Condenser Water Entry Temp, Condensor Flow, Compressor Lead/Lag)

Model Chiller Amps/Power

Chiller Amps/Power = f(Evaporator Leaving Temp, Chiller Load, Condenser Water Entry Temp, Condensor Flow)

Model Compressor Amps

Compressor Amps = f(Suction Pressure, Discharge Pressure, Chiller Load, Compressor Lead/Lag)

Model Condenser Leaving

Condenser Leaving = f(Chiller Load, Condenser water entry, Condensor Flow, Compressor Lead/Lag)

Before you diagnose

Only run these rules when the chiller is running steady, load is above minimum, flows are valid, and you’re not in a setpoint change.

Also require the pattern to hold for a while (ex: 20–30 minutes) before calling it a fault.

Step-by-step isolation rules

Step 1 — Start with Power (efficiency symptom)

- If Power residual is NOT high → no efficiency fault (stop here).

- If Power residual IS high → go to Step 2.

Step 2 — Check if the extra power is caused by high head pressure

2A) If Discharge Pressure residual is high

This means the chiller is running at higher head pressure than normal, which usually drives up power.

Now look at Condenser Water Leaving residual to decide why head is high:

- If CW Leaving residual is also high

→ Condenser water-side problem (heat not being rejected well to the condenser water).

Then:

  - If it’s spike/intermittent → likely low condenser flow.

  - If it’s steady and slowly getting worse over weeks → likely condenser fouling.

- If CW Leaving residual is near normal (around zero)

→ Refrigerant-side high head (overcharge / non-condensables bucket).

(Because the water loop looks normal, but head pressure is still higher than expected.)

- If CW Leaving residual is noisy/inconsistent

→ call it High head – ambiguous (needs ops confirmation).

Note: DT residual is only a “support” signal. Don’t rely on it to separate high head causes.

2B) If

Discharge Pressure residual is NOT high

So power is high, but it’s not because head pressure is unusually high.

Now check Compressor Amps and Suction Pressure.

Step 3 — Decide compressor vs evaporator-side issue

3A) Compressor inefficiency (mechanical/electrical)

If all are true:

- Power residual is high

- Compressor Amps residual is high

- Discharge Pressure residual is near normal

- Suction Pressure residual is near normal

→ Compressor inefficiency / motor-mechanical loss

(Meaning: for the same operating pressures, the compressor is drawing more current than normal.)

3B) Evaporator-side / starved evaporator (undercharge vs feed issue)

If:

- Power residual is high

- Discharge Pressure residual is near normal

- Suction Pressure residual is low (lower than expected)

→ Starved evaporator / evaporator-side problem

Then separate:

- If suction (and often DT) residuals are highly oscillatory / unstable

→ Expansion valve hunting / unstable control

- If suction stays low steadily for hours/days

→ Persistent starvation: undercharge vs restriction/underfeeding

(You can’t cleanly split undercharge vs restriction with the sensors you have, so keep it as a combined label.)

Step 4 — “Data/sensor mismatch” checks (so you don’t mislabel)

These can be flagged even when power isn’t high:

- If DP residual is high, but Power, DT, and CW Leaving residuals are all normal

→ DP sensor bias or DP model mismatch

- If DT residual is abnormal, but Power, Amps, and DP residuals are normal

→ DT sensor bias / measurement point changed

The quick cheat version (fast fingerprints)

- Condenser water-side: Power ↑, DP ↑, CW Leaving ↑

- Refrigerant-side high head: Power ↑, DP ↑, CW Leaving ~ normal

- Compressor inefficiency: Power ↑, Amps ↑, DP ~ normal, SP ~ normal

- Starved evap (undercharge / EXV underfeed): SP ↓ (key), often DT unstable/high; DP ~ normal

- EXV hunting: SP and/or DT residuals swing up/down repeatedly

- DP sensor issue: DP residual weird, everything else normal

- DT sensor issue: DT residual weird, everything else normal

Scope and non-goals

Goal: Determine a single primary fault/condition (or “no diagnosis”) using exactly 6 model residuals:

- rPwr (Chiller Power)

- rDP (Discharge Pressure)

- rSP (Suction Pressure)

- rDT (Discharge Temperature)

- rAmp (Compressor Amps)

- rCWL (Condenser Water Leaving Temp)

Residual definition:

rX(t) = X_actual(t) − X_pred(t) where X_pred is from a normal-operation model.

Non-goals: Perfect separation of undercharge vs EXV restriction vs hunting (limited sensors). We label ambiguity honestly.

1) Inputs required

1.1 Raw sensor tags (per timestep)

Minimum tags needed to compute model inputs and gates:

- DP, SP, DT

- Compressor Amps (or compressor current)

- Chiller Power (kW from external meter if present; else chiller kW estimate)

- Evaporator entering water temp (EWT_in)

- Evaporator leaving water temp (EWT_out)

- Evaporator flow OR Evap DPT (site-specific)

- Condenser entering water temp (CWT_in) (water-cooled) OR OAT (air-cooled variant not covered here)

- Condenser leaving water temp (CWT_out = CW Leaving)

- Condenser flow (CW Flow)

- Lead/Lag (or staging indicator)

- Chiller run status (on/off)

- Alarms/limit mode status (if available)

- Setpoint (only for gating: transitions / stable periods)

1.2 Derived values

- Evap_dT = EWT_in − EWT_out

- Cond_dT = CWT_out − CWT_in

- Load_calc (site formula; typically EvapFlow * Evap_dT * k, where k includes densityCpunit conversion)

2) “Normal models” (frozen structure)

Dev team should implement training + inference for each model per site/chiller.

2.1 Final validated model forms

- DP model: DP = f(SP, Load_calc, CWT_in, CW_Flow, Lead/Lag)

- SP model (site template):

  - Flow site: SP = f(EWT_in, EWT_out, EvapFlow, Lead/Lag)

  - DPT site: SP = f(EWT_in, EWT_out, EvapDPT, Lead/Lag)

- DT model: DT = f(SP, DP, Load_calc, Lead/Lag) (optional + CWT_in if reduces seasonal bias)

- Power model: Pwr = f(EWT_out, Load_calc, CWT_in, CW_Flow)

- Amp model: Amp = f(SP, DP, Load_calc, Lead/Lag)

- CWL model: CWT_out = f(CWT_in, Load_calc, CW_Flow, Lead/Lag)

Important design constraints

- Do not include CWT_out in DP model.

- Do not include DT in CWL model.

- Do not include DP/SP/DT in the Power model.

3) Residual normalization (robust z-scores)

3.1 Compute robust stats on “normal” data

For each residual rX, compute:

- med_X = median(rX on normal periods)

- mad_X = median(|rX − med_X|)

Set mad_X = max(mad_X, eps) to avoid divide-by-zero.

3.2 Normalize

zX(t) = (rX(t) − med_X) / mad_X

(If your team prefers σ-based z-scores, that’s acceptable, but MAD is recommended.)

4) Time-window features (level / persistence / volatility / trend)

Pick a base timestep (recommend 1–5 minutes). Use rolling windows:

4.1 Level (smoothed residual)

Lx(t) = rolling_mean(zX, W_level)

Default: W_level = 10 minutes

4.2 Persistence (fault presence)

Over last W_persist:

- Px_high = fraction(Lx > T_high)

- Px_low  = fraction(Lx < -T_low)

Default: W_persist = 30 minutes, require ≥ 0.8

4.3 Volatility (hunting)

Vx(t) = rolling_std(zX, W_vol)

Default: W_vol = 10 minutes

4.4 Trend (fouling vs flow)

Compute daily/weekly slope on a smoothed series:

- Lx_1h = rolling_mean(zX, 1 hour)

- Sx = slope(Lx_1h over W_trend)

Default: W_trend = 14–30 days

5) Operational gates (if any fail → output “NO DIAGNOSIS”)

Run diagnosis only when all gates are true.

5.1 Gates

- Running gate: chiller is ON

- Stability gate: not starting/stopping, no rapid ramp (site-defined), not in limit/alarm mode

- Load gate: Load_calc > Load_min (typical 15–25% of design)

- Flow validity gate: evap + condenser flow (or DPT) are valid

- Transition gate: not within setpoint transition window (site-defined)

5.2 Persistence requirement

Even if logic triggers, only assert a fault if it persists:

- Fast faults: ≥ 10–30 min

- Fouling: hours/days + requires trend

6) Thresholds (defaults)

All thresholds are on Lx (smoothed z-scores).

- T_high = +2.0 (warning), +3.0 (strong)

- T_0 = 0.8 to 1.0 (near-zero band)

- T_sp_low = 2.0 (so “low suction” means Lsp < -2.0)

- T_vol = 1.8–2.5 (tune per sampling)

- Persist_frac = 0.8

7) Decision logic (one-primary-fault)

Implement as a deterministic priority-ordered function.

7.1 Helper booleans (computed at time t)

Using Lx(t):

- PWR_HIGH = (Lpwr > T_high)

- DP_HIGH  = (Ldp  > T_high)

- SP_LOW   = (Lsp  < -T_sp_low)

- AMP_HIGH = (Lamp > T_high)

- CWL_HIGH = (Lcwl > T_high)

- CWL_NEAR0 = (abs(Lcwl) <= T_0)

- DP_NEAR0 = (abs(Ldp) <= T_0)

- SP_NEAR0 = (abs(Lsp) <= T_0)

- DT_ABS_HIGH = (abs(Ldt) > T_high) (for sensor buckets)

Volatility:

- SP_VOL_HIGH = (Vsp > T_vol)

- DT_VOL_HIGH = (Vdt > T_vol)

- CWL_VOL_HIGH = (Vcwl > T_vol) (optional)

- DP_VOL_HIGH = (Vdp > T_vol) (optional)

Trend (for fouling split):

- DP_TREND_UP  = (Sdp > S_thresh)

- CWL_TREND_UP = (Scwl > S_thresh)

Choose S_thresh by commissioning on normal data.

7.2 Priority order

Priority 0 — Sensor/model mismatch “savers”

These can run even if PWR is not high.

F) DP sensor bias / DP model mismatch

Trigger if:

- abs(Ldp) > T_high

- AND abs(Lpwr) <= T_0

- AND abs(Ldt) <= T_0

- AND abs(Lcwl) <= T_0

Output: DP_SENSOR_OR_MODEL_MISMATCH

G) DT sensor bias / DT measurement change

Trigger if:

- abs(Ldt) > T_high

- AND abs(Lpwr) <= T_0

- AND abs(Lamp) <= T_0

- AND abs(Ldp) <= T_0

Output: DT_SENSOR_OR_MEAS_POINT_CHANGE

If either triggers → return immediately.

Priority 1 — Efficiency entry (Power)

If PWR_HIGH == false:

- Output: NO_EFFICIENCY_FAULT

- (Optionally include “info” flags from sensor buckets already handled.)

If PWR_HIGH == true: proceed.

Priority 2 — Head-driven split

Branch A: Head-driven (DP high)

If DP_HIGH:

A1) Condenser water-side issue

If CWL_HIGH:

- Primary output: CONDENSER_WATER_SIDE

Then split:

- If (DP_VOL_HIGH OR CWL_VOL_HIGH) AND NOT (DP_TREND_UP OR CWL_TREND_UP):

  - Output: CONDENSER_LOW_FLOW

- Else if (DP_TREND_UP OR CWL_TREND_UP) AND NOT high volatility:

  - Output: CONDENSER_FOULING

- Else:

  - Output: CONDENSER_WATER_SIDE_UNSPECIFIED

A2) Refrigerant-side high head

Else if CWL_NEAR0:

- Output: REFRIGERANT_SIDE_HIGH_HEAD (overcharge vs non-condensables bucket)

A3) Ambiguous high head

Else:

- Output: HIGH_HEAD_AMBIGUOUS

Return.

Branch B: Power high but not head-driven (DP near 0)

If DP_NEAR0:

B1) Compressor inefficiency

If AMP_HIGH AND SP_NEAR0:

- Output: COMPRESSOR_INEFFICIENCY

Return.

B2) Starved evap / evap-side bucket

If SP_LOW:

- If SP_VOL_HIGH OR DT_VOL_HIGH:

  - Output: EXV_HUNTING_OR_UNSTABLE_CONTROL

- Else:

  - Output: STARVED_EVAP_UNDERCHARGE_OR_RESTRICTION

Return.

B3) Power high unexplained

Else:

- Output: POWER_HIGH_UNEXPLAINED

Return.

Safety fallback

If neither DP_HIGH nor DP_NEAR0 (i.e., DP is moderately positive but not “high”):

- You may treat as ambiguous or use a “mid-band” rule:

  - If CWL_HIGH → water-side likely

  - Else if CWL_NEAR0 → refrigerant-side likely

  - Else ambiguous

(But simplest is to widen DP_NEAR0 band or tighten DP_HIGH.)

8) Output contract (what the service returns)

For each scoring interval (e.g., every 5 minutes), return:

8.1 Required fields

- timestamp

- primary_condition_code (enum from section 7)

- state ∈ {NO_DIAGNOSIS, NORMAL, FAULT}

- confidence (0–1) (optional but recommended)

8.2 Recommended supporting fields (debuggable + ops-friendly)

- triggered_rules (list of rule IDs)

- key_evidence dictionary with current L-values:

  - Lpwr, Ldp, Lsp, Lamp, Lcwl, Ldt

- persistence_metrics (Px values)

- volatility_metrics (Vx values)

- trend_metrics (Sdp, Scwl, etc. if used)

Confidence suggestion (simple, deterministic):

- Start at 0.6 when rule triggers

- Add +0.1 for each strong supporting condition met (e.g., CWL_NEAR0 for refrigerant-side, trend for fouling, etc.)

- Cap at 0.95

- Reduce if near thresholds or if gates barely pass

9) Commissioning & QA checklist (what to test before deployment)

9.1 Model QA (per model)

- Residual mean near 0 on normal data

- Residual vs driver flatness

- Performance stable by load bin and lead/lag

9.2 Rule QA (end-to-end)

- Run on at least 2–4 weeks of “known good” data:

  - low false-positive rate after gates

- Replay known events if available:

  - condenser low flow/fouling → CONDENSER_*

  - suspected high head without CWL rise → REFRIGERANT_SIDE_HIGH_HEAD

  - compressor electrical issue → COMPRESSOR_INEFFICIENCY

  - hunting → EXV_HUNTING_OR_UNSTABLE_CONTROL

9.3 Alarm hygiene

- Enforce persistence before raising fault

- Add hysteresis (clear fault only when L-values fall below a lower threshold for a sustained period)

10) Notes for devs (to avoid common mistakes)

- Never use predicted DP as an input to other models; always use measured DP/SP where required.

- Don’t score during transitions/start-stop (biggest noise source).

- Treat undercharge vs restriction as one bucket unless you add superheat/subcooling/purge signals.

- Since load is calculated, treat flow/temp validity as first-class gating.